## Substation List
Brief Notes on RE Evacuation Capacity
1) 100% of the transformation capacity of a substation is allowed for RE evacuation with a limit of not more than 50% in each bus. However, the capcities given below are only tentative capacities and grid connectivity will be issued subject to technical load flow studies for each case separately
2) Out of the list of spare bays available in the tables, required number of bays will be reserved for next five years requirement of Transco and remaining bays and the land available for future bays will be allotted to RE generators.
3) In case of scarcity of bays, installation of PASS Modules for bays will be considered for RE evacuation at the cost of generators.
Circle wise RE Evacuation Capacity
Sl.No. | Name of the Circle | Name of Substation | PTR Capacity in MVA |  | Voltage level of Bus | PTR Capacity in MW (pf:0.95) | 50% of PTR capacity for RE injection in each bus | Existing RE inection Capacity to the bus | Balance capacity available for RE injection | No.of Spare bays available (Voltage wise) | Land availability in any for future bays
1 | Adilabad | 400/220KV SS Nirmal | 3x315 = 945MVA | 945 | 400kV | 897.75 | 448.875 | 0 | 448.875 | - | 1
[5 empty] | 220kV |  | 448.875 | 0 | 448.875 | - | 1
2 |  | 220/132/33KV SS Nirmal | 1X160+2X100 = 360MVA | 360 | 220kV | 342 | 171 | 0 | 171 | - | -
|  |  | 1X31.5+ 2X50 = 131.5MVA |  | 132kV |  | 171 | 50 | 121 | - | 2
|  |  |  | 131.5 | 33 KV | 124.925 | 62.4625 | 50 | 12.4625
3 |  | 220/132KV SS Indravelly | 2X100 = 200MVA | 200 | 220kV | 190 | 95 | 0 | 95 | 2 | 1
[5 empty] | 132kV |  | 95 | 0 | 95 | - | 2
4 |  | 132/33KV SS Bhainsa | 1X31.5+ 1X50 = 81.5MVA | 81.5 | 132kV | 77.425 | 38.7125 | 0 | 38.7125 | - | -
[5 empty] | 33kV |  | 38.71 | 15 | 23.71 | 1 | 1
5 |  | 132/33KV SS Ichoda | 3x16 = 48MVA | 48 | 132kV | 45.6 | 22.8 | 0 | 22.8 | - | 2
[5 empty] | 33kV |  | 22.8 | 0 | 22.8 | 1 | 1
6 |  | 132/33KV SS Adilabad | 3X31.5 MVA = 94.5MVA | 94.5 | 132kV | 89.775 | 44.8875 | 0 | 44.8875 | - | -
[5 empty] | 33kV |  | 44.89 | 0 | 44.89 | - | -
7 |  | 132/33KV SS Mudhole | 2X10/16 = 32 MVA | 32 | 132kV | 30.4 | 15.2 | 0 | 15.2 | - | 1
[5 empty] | 33kV |  | 15.2 | 0 | 15.2 | - | 2
8 |  | 132/33KV SS Khanapur | 2X31.5 =63MVA | 63 | 132kV | 59.85 | 29.925 | 0 | 29.925 | - | -
[5 empty] | 33kV |  | 29.93 | 0 | 29.93 | 1 | 1
9 |  | 132/33KV SS Burugupally | 2X31.5 = 63MVA | 63 | 132kV | 59.85 | 29.925 | 0 | 29.925 | - | 1
[5 empty] | 33kV |  | 29.93 | 0 | 29.93 | 1 | 2
10 |  | 132/33KV SS Sarangapur | 3x10/16 =48MVA | 48 | 132kV | 45.6 | 22.8 | 0 | 22.8 | 2 | -
[5 empty] | 33kV |  | 22.8 | 0 | 22.8 | 1 | 1
11 |  | 132/33KV SS Utnoor | 2X10/16 = 32MVA | 32 | 132kV | 30.4 | 15.2 | 0 | 15.2 | - | -
[5 empty] | 33kV |  | 15.2 | 0 | 15.2 | - | 2
12 |  | 132/33KV SS Mancherial | 31.5+50 =81.5MVA | 81.5 | 132KV | 77.425 | 38.7125 | 0 | 38.7125 | 1 | 3
[5 empty] | 33KV |  | 38.71 | 0 | 38.71 | 1 | 3
13 |  | 132/33KV SS Luxettipet | 31.5+50 =81.5MVA | 81.5 | 132KV | 77.425 | 38.7125 | 0 | 38.7125 | - | 1
[5 empty] | 33KV |  | 38.71 | 0 | 38.71 | 2 | -
14 |  | 132/33KV SS Chennur | 31.5+31.5 =63MVA | 63 | 132KV | 59.85 | 29.925 | 0 | 29.925 | - | 2
[5 empty] | 33KV |  | 29.93 | 11 | 18.93 | - | 4
15 |  | 132/33KV SS Bellampally | 2*31.5MVA =63MVA | 63 | 132KV | 59.85 | 29.925 | 0 | 29.925 | 1 | 2
[5 empty] | 33KV |  | 29.93 | 30 | -0.07 | - | 2
16 |  | 132/33KV Sirpur Kagaznagar | 16+31.5 =47.5MVA | 47.5 | 132KV | 45.125 | 22.5625 | 0 | 22.5625 | - | 2
[5 empty] | 33KV |  | 22.56 | 0 | 22.56 | 2 | -
17 |  | 132/33KV SS Asifabad | 10/16+10/16 =32MVA | 32 | 132KV | 30.4 | 15.2 | 0 | 15.2 | - | 2
[5 empty] | 33KV |  | 15.2 | 0 | 15.2 | 3 | 2
18 |  | 220/132KV SS Bellampally (Mandamary) | 3*100MVA =300MVA | 300 | 220KV | 285 | 142.5 | 67.5 | 75 | 1 | 2
[5 empty] | 132KV |  | 142.5 | 125.5 | 17 | 2 | 1
19 | Karimnagar | 132/33kV SS Jagtial | 1x31.5+2x50 = 131.5 | 131.5 | 132kV | 124.925 | 62.4625 | 30 | 32.4625 | 0 | 0
[5 empty] | 33kV |  | 62.4625 | 0 | 62.4625 | 0 | 1
20 |  | 220/132kV SS Jagtial | 3x100+1x160 =460 | 460 | 220kV | 437 | 218.5 | 0 | 218.5 | 0 | 0
[5 empty] | 132kV |  | 218.5 | 0 | 218.5 | 1 | 0
21 |  | 132/33kV SS Pudur | 2x31.5+1x16=79 | 79 | 132kV | 75.05 | 37.525 | 0 | 37.525 | 2 | 0
[5 empty] | 33kV |  | 37.525 | 0 | 37.525 | 1 | 1
22 |  | 132 /33 KV Dharmapuri | 2x31.5+1x16=79 | 79 | 132 KV | 75.05 | 37.525 | 0 | 37.525 | 2 | 3
[5 empty] | 33 KV |  | 37.525 | 0 | 37.525 | 1 | 4
23 |  | 132/33kV SS Raikal | 1x16+1x31.5=47.5 | 47.5 | 132 KV | 45.125 | 22.5625 | 0 | 22.5625 | 2 | 3
[5 empty] | 33 KV |  | 22.5625 | 0 | 22.5625 | 2 | 4
24 |  | 132/33kV SS Kathalapur | 2x31.5+1x16=79 | 79 | 132 KV | 75.05 | 37.525 | 0 | 37.525 | 2 | 0
[5 empty] | 33 KV |  | 37.525 | 0 | 37.525 | 0 | 2
25 |  | 132/33kV SS Korutla | 1x31.5+1x50=81.5 | 81.5 | 132 KV | 77.425 | 38.7125 | 0 | 38.7125 | 2 | 0
[5 empty] | 33 KV |  | 38.7125 | 0 | 38.7125 | 3 | 4
26 |  | 132/33kV SS Godur | 2x50=100 | 100 | 132 KV | 95 | 47.5 | 0 | 47.5 | 1 | 2
[5 empty] | 33 KV |  | 47.5 | 25 | 22.5 | 0 | 0
27 |  | 132/33kV SS Chippalapalli | 1x31.5+2x16=63.5 | 63.5 | 132 KV | 60.325 | 30.1625 | 0 | 30.1625 | 0 | 3
[5 empty] | 33 KV |  | 30.1625 | 0 | 30.1625 | 0 | 4
28 |  | 132/33kV SS Yellareddypet | 2x31.5+1x16=79 | 79 | 132 KV | 75.05 | 37.525 | 0 | 37.525 | 0 | 1
[5 empty] | 33 KV |  | 37.525 | 0 | 37.525 | 3 | 2
29 |  | 132/33kV SS Mallaram | 1x31.5+1x50=81.5 | 81.5 | 132 KV | 77.425 | 38.7125 | 0 | 38.7125 | 0 | 3
[5 empty] | 33 KV |  | 38.7125 | 15 | 23.7125 | 0 | 0
30 |  | 132/33kV SS Nimmapally | 2x16=32 | 32 | 132 KV | 30.4 | 15.2 | 0 | 15.2 | 2 | 1
[5 empty] | 33 KV |  | 15.2 | 0 | 15.2 | 3 | 4
31 |  | 220/132/33KV SS Sircilla | 3x100=300 MVA(200/132KV) | 300 | 220KV | 285 | 142.5 | 0 | 142.5 | 2 | 0
[5 empty] | 132KV |  | 142.5 | 30 | 112.5 | 1 | 0
|  |  | 3x50=150 MVA(132/33KV) | 150 | 33KV | 142.5 | 71.25 | 0 | 71.25 | 1 | 1
32 |  | 132/33 KV SS Karimnagar | 1x50+2x31.5=113 | 113 | 132KV | 107.35 | 53.675 | 0 | 53.675 | 0 | 0
[5 empty] | 33KV |  | 53.68 | 0 | 53.68 | 0 | 2
33 |  | 132/33 KV SS Jammikunta | 1×50+1×31.5=81.5 | 81.5 | 132KV | 77.425 | 38.7125 | 0 | 38.7125 | 0 | 2
[5 empty] | 33KV |  | 38.71 | 0 | 38.71 | 0 | 0
34 |  | 132/33 KV SS Manakondoor | 1x31.5+1x50 | 81.5 | 132KV | 77.425 | 38.7125 | 0 | 38.7125 | 1 | 0
[5 empty] | 33KV |  | 38.71 | 0 | 38.71 | 0 | 2
35 |  | 132/33 KV SS Huzurabad | 1×50+1×31.5=81.5 | 81.5 | 132KV | 77.425 | 38.7125 | 0 | 38.7125 | 0 | 1
[5 empty] | 33KV |  | 38.71 | 0 | 38.71 | 0 | 0
36 |  | 132/33 KV SS Waterworks | 2x31.5=63 | 63 | 132KV | 59.85 | 29.925 | 0 | 29.925 | 0 | 4
[5 empty] | 33KV |  | 29.93 | 0 | 29.93 | 1 | 4
37 |  | 132/33 KV SS Suglampally | 1x50+2x31.5=113 | 113 | 132KV | 107.35 | 53.675 | 0 | 53.675 | 0 | 2
[5 empty] | 33KV |  | 53.68 | 0 | 53.68 | 2 | 2
38 |  | 132/33 KV SS Dharmaram | 1x31.5+1x16=79 | 79 | 132KV | 75.05 | 37.525 | 0 | 37.525 | 1 | 2
[5 empty] | 33KV |  | 37.53 | 0 | 37.53 | 4 | 0
39 |  | 132/33 KV SS Ellanthakunta | 2x31.5=63 | 63 | 132KV | 59.85 | 29.925 | 0 | 29.925 | 0 | 0
[5 empty] | 33KV |  | 29.93 | 0 | 29.93 | 0 | 0
40 |  | 132/33 KV SS Husnabad | 1x50+2x31.5=113 | 113 | 132KV | 107.35 | 53.675 | 0 | 53.675 | 0 | 0
[5 empty] | 33KV |  | 53.68 | 0 | 53.68 | 2 | 0
41 |  | 132/33 KV SS Shanigaram | 2x31.5+1x16=79 | 79 | 132KV | 75.05 | 37.525 | 0 | 37.525 | 0 | 3
[5 empty] | 33KV |  | 37.53 | 15 | 22.53 | 3 | 4
42 |  | 132/33 KV SS Kamalapur | 2x31.5 = 63 | 63 | 132KV | 59.85 | 29.925 | 0 | 29.925 | 1 | 0
[5 empty] | 33KV |  | 29.93 | 0 | 29.93 | 3 | 4
43 |  | 132/33 KV SS Mulkanoor | 2x31.5 | 63 | 132KV | 59.85 | 29.925 | 30 | -0.075 | 0 | 1
[5 empty] | 33KV |  | 29.93 | 0 | 29.93 | 2 | 0
44 |  | 132/33 KV SS Kachapur | 3x16=48 | 48 | 132KV | 45.6 | 22.8 | 0 | 22.8 | 1 | 0
[5 empty] | 33KV |  | 22.8 | 0 | 22.8 | 3 | 2
45 |  | 132/33KV SS Jangapally | 3x16=48 | 48 | 132KV | 45.6 | 22.8 | 0 | 22.8 | 0 | 2
[5 empty] | 33KV |  | 22.8 | 0 | 22.8 | 1 | 2
46 |  | 132/33KV SS Padmanagar | 1x50+1x16=66 | 66 | 132KV | 62.7 | 31.35 | 0 | 31.35 | 1 | 3
[5 empty] | 33KV |  | 31.35 | 0 | 31.35 | 0 | 4
47 |  | 220/132/33 KV SS Durshed | 3x160MVA =480MVA. 2x31.5MVA=63MVA | 480 | 220KV | 456 | 228 | 0 | 228 | 0 | 0
[5 empty] | 132KV |  | 228 | 0 | 228 | 0 | 0
|  |  |  | 63 | 33KV | 59.85 | 29.925 | 0 | 29.925 | 0 | 2
48 |  | 220/132KV SS Huzurabad | 2x100+1x160 = 360 | 360 | 220KV | 342 | 171 | 0 | 171 | 0 | 2
[5 empty] | 132KV |  | 171 | 0 | 171 | 2 | 0
49 |  | 220/132 KV SS Malyalapally | 2X160 =320 | 320 | 220KV | 304 | 152 | 0 | 152 | 0 | 0
[5 empty] | 132KV |  | 152 | 0 | 152 | 0 | 0
50 |  | 132KV SS Manthani | 2 X 50 = 100 | 100 | 132KV | 95 | 47.5 | 22 | 25.5 | 0 | 1
[5 empty] | 33KV |  | 47.5 | 25 | 22.5 | 0 | 0
51 |  | 132/33 KV SS RTS-B | 1 X16+1X31.5 =47.5 | 47.5 | 132KV | 45.125 | 22.5625 | 0 | 22.5625 | 0 | 0
[5 empty] | 33KV |  | 22.56 | 0 | 22.56 | 0 | 1
52 |  | 132/33 KV SS Kalwasrirampur | 1 X 31.50 + 1 X 50 = 81.5 | 81.5 | 132KV | 77.425 | 38.7125 | 0 | 38.7125 | 1 | 0
[5 empty] | 33KV |  | 38.71 | 15 | 23.71 | 2 | 4
53 |  | 220 KV SS Manthani | 3X 100 = 300 | 300 | 220KV | 285 | 142.5 | 0 | 142.5 | 0 | 0
[5 empty] | 132KV |  | 142.5 | 37 | 105.5 | 3 | 0
54 |  | 33/132KV SS NTPC Solar SS | 1 X16 =16 | 16 | 33KV | 15.2 | 7.6 | 0 | 7.6 | 0 | 0
[5 empty] | 132KV | 15.2 | 7.6 | 0 | 7.6 | 0 | 1
55 |  | 132KV SS Kamanpur | 2 X 16 = 32 | 32 | 132KV | 30.4 | 15.2 | 0 | 15.2 | 0 | 2
[5 empty] | 33KV |  | 15.2 | 0 | 15.2 | 1 | 4
56 |  | 132KV Kataram | 2 X 50=100 | 100 | 132KV | 95 | 47.5 | 0 | 47.5 | 0 | 3
[5 empty] | 33kV |  | 47.5 | 0 | 47.5 | 0 | 4
57 | Khammam | 132KV SS Khammam | 3×50=150 | 150 | 132KV | 142.5 | 71.25 | 0 | 71.25 | 0 | 0
[5 empty] | 33KV |  | 71.25 | 0 | 71.25 | 1 (with out equipment) | 0
58 |  | 132KV SS Arempula | 2x 16 + 1x31.5 | 63.5 | 132KV | 60.325 | 30.1625 | 0 | 30.1625 | 0 | 1
[5 empty] | 33KV |  | 30.16 | 0 | 30.16 | 2 | 1
59 |  | 132KV SS Pammy | 1x31.5 +1x10/16 | 47.5 | 132KV | 45.125 | 22.5625 | 0 | 22.5625 | 0 | 2
[5 empty] | 33KV |  | 22.56 | 0 | 22.56 | 0 | 4
60 |  | 132KV SS Thallada | 2x50 | 100 | 132KV | 95 | 47.5 | 0 | 47.5 | 0 | 2
[5 empty] | 33KV |  | 47.5 | 0 | 47.5 | 2 (structure without equipment) | 0
61 |  | 132KV SS Madhira | 2x31.5 | 63 | 132KV | 59.85 | 29.925 | 0 | 29.925 | 0 | 0
[5 empty] | 33KV |  | 29.93 | 0 | 29.93 | 0 | 2
62 |  | 132KV SS Kusumanchi | 3x50 | 100 | 132KV | 95 | 47.5 | 0 | 47.5 | 0 | 0
[5 empty] | 33KV |  | 47.5 | 0 | 47.5 | 0 | 1
61 |  | 220KV SS Kallur | 2x100 | 200 | 220KV | 190 | 95 | 0 | 95 | 0 | 2
[5 empty] | 132KV |  | 95 | 32.5 | 62.5 | 0 | 0
|  |  | 2x31.5 | 63 | 33KV | 59.85 | 29.925 | 0 | 29.925 | 1 (with structure and equipment) | 4
62 |  | 220KV SS Budidampadu | 2x 160MVA | 320 | 220KV | 304 | 152 | 0 | 152 | 0 | 0
[5 empty] | 132KV |  | 152 | 0 | 152 | 0 | 0
63 |  | 220KV SS Peddagopathi | 2x100 | 200 | 220KV | 190 | 95 | 0 | 95 | 0 | 0
[5 empty] | 132KV |  | 95 | 0 | 95 | 1 (with structure) | 1
|  |  | 2x31.5 | 63 | 33KV | 59.85 | 29.925 | 0 | 29.925 | 1 (with structure and equipment) | 3
64 |  | 220/132/33KV SS Aswaraopeta | 2x100 | 200 | 220KV | 190 | 95 | 0 | 95 | 0 | 0
[5 empty] | 132KV |  | 95 | 0 | 95 | 0 | 2
|  |  | 2x 31.5 | 63 | 33KV | 59.85 | 29.925 | 0 | 29.925 | 0 | 2
65 |  | 132/33KV SS B.Gangaram | 2*50MVA | 100 | 132KV | 95 | 47.5 | 0 | 47.5 | 0 | 0
[5 empty] | 33KV |  | 47.5 | 0 | 47.5 | 0 | 2
66 |  | 132/33KV SS Penubally | 2*50MVA | 100 | 132KV | 95 | 47.5 | 0 | 47.5 | 0 | 0
[5 empty] | 33KV |  | 47.5 | 0 | 47.5 | 0 | 0
67 |  | 400/220KV SS ASUPAKA | 2 X 315MVA = 630MVA | 630 | 400KV | 598.5 | 299.25 | 0 | 299.25 | 3 ( W/O E) | 0
[5 empty] | 220KV | 598.5 | 299.25 | 0 | 299.25 | 2+2 (W/E) | 0
68 |  | 400KVSS JULURPADU | 2X315=630 | 630 | 400KV | 598.5 | 299.25 | 0 | 299.25 | 0 | 4
[5 empty] | 220KV | 598.5 | 299.25 | 0 | 299.25 | 0 | 4
69 |  | 220KV SS MANUGURU | 2X160 | 320 | 220KV | 304 | 152 | 0 | 152 | 0 | 2
[5 empty] | 132KV |  | 152 | 30 | 122 | 0 | 1
|  |  | 2X50 | 100 | 33KV | 95 | 47.5 | 0 | 47.5 | 0 | 2
70 |  | 220KV SS SEETHARAMPATNAM | 2X100 | 200 | 220KV | 190 | 95 | 0 | 95 | 0 | 0
[5 empty] | 132KV |  | 95 | 37 | 58 | 0 | 1
|  |  | 2X50 | 100 | 33KV | 95 | 47.5 | 0 | 47.5 | 0 | 1
71 |  | 132/33KV SS YELLANDU | 2X50=100 | 100 | 132KV | 95 | 47.5 | 39 | 8.5 | 0 | 2
[5 empty] | 33KV |  | 47.5 | 15 | 32.5 | 0 | 2
72 |  | 132/33KV RTSS KOTHAGUDEM | 1X50=50 | 50 | 132KV | 47.5 | 23.75 | 0 | 23.75 | 0 | 0
[5 empty] | 33KV |  | 23.75 | 0 | 23.75 | 0 | 0
73 |  | 132/33KV CHANDRUGONDA | 1X31.5+1X10/16=47.5 | 47.5 | 132KV | 45.125 | 22.5625 | 22.5 | 0.0625 | 0 | 2
[5 empty] | 33KV |  | 22.56 | 0 | 22.56 | 0 | 4
74 |  | 132/33KV BHADRACHALAM | 1X31.5+1X10/16=47.5 | 47.5 | 132KV | 45.125 | 22.5625 | 0 | 22.5625 | 0 | 1
[5 empty] | 33KV |  | 22.56 | 0 | 22.56 | 0 | 4
75 |  | 132/33KV NVPURAM | 2X10/16=32 | 32 | 132KV | 30.4 | 15.2 | 0 | 15.2 | 0 | 1
[5 empty] | 33KV |  |  | 0 | 0 | 0 | 4
76 | Mahaboobnagar | 400/220 KV SS Veltoor | 2*500+2*315 | 1630 | 400KV | 1548.5 | 774.25 |  | 774.25 | 0 | 0
[5 empty] | 220KV |  | 774.25 | 400 | 374.25 | 2 | 0
77 |  | 220/132 KV SS Jurala | 1*160+2*100 | 360 | 220KV | 342 | 171 |  | 171 | 2 | 2
[5 empty] | 132KV |  | 171 |  | 171 | 0 | 0
78 |  | 132/33 KV SS Gadwal | 1*80+1*50 | 130 | 132KV | 123.5 | 61.75 |  | 61.75 | 1 | 1
[5 empty] | 33KV |  | 61.75 | 35 | 26.75 | 4 | 0
79 |  | 132/33 KV SS Amarachinta | 1*31.5+1*16 | 37.5 | 132KV | 35.625 | 17.8125 |  | 17.8125 | 2 | 2
[5 empty] | 33KV |  | 17.81 |  | 17.81 | 2 | 4
80 |  | 132/33 KV SS Ieeja | 1*50+2*31.5 | 113 | 132KV | 107.35 | 53.675 | 35 | 18.675 | 0 | 0
[5 empty] | 33KV |  | 53.68 |  | 53.68 | 2 | 1
81 |  | 132/33 KV SS Alampur | 2*31.5 | 63 | 132KV | 59.85 | 29.925 |  | 29.925 | 1 | 4
[5 empty] | 33KV |  | 29.93 | 21 | 8.93 | 6 | 2
82 |  | 132/33 KV SS Ganganpally | 1*50+1*31.5 | 81.5 | 132KV | 77.425 | 38.7125 |  | 38.7125 | 3 | 3
[5 empty] | 33KV |  | 38.71 |  | 38.71 | 3 | 8
83 |  | 220/132/33 KV SS Wanaparthy | 2*160 | 320 | 220KV | 304 | 152 |  | 152 | 0 | 0
[5 empty] | 132KV |  | 152 | 100 | 52 | 0 | 0
|  |  | 2*80 | 160 | 33KV | 152 | 76 |  | 76 | 0 | 0
84 |  | 132/33 KV SS Khillaghanpur | 2*31.5 | 63 | 132KV | 59.85 | 29.925 |  | 29.925 | 1 | 3
[5 empty] | 33KV |  | 29.93 | 15 | 14.93 | 4 | 2
85 |  | 132/33 KV SS Thirumalaipally | 2*31.5+1*16 | 79 | 132KV | 75.05 | 37.525 | 28.2 | 9.325 | 0 | 0
[5 empty] | 33KV |  | 37.53 |  | 37.53 | 0 | 0
86 |  | 132/33 KV SS Peddadagada | 2*31.5 | 63 | 132KV | 59.85 | 29.925 |  | 29.925 | 0 | 3
[5 empty] | 33KV |  | 29.93 |  | 29.93 | 3 | 4
87 |  | 220/33 KV SS Singotam | 1*50+1*31.5 | 81.5 | 220KV | 77.425 | 38.7125 |  | 38.7125 | 0 | 2
[5 empty] | 33KV |  | 38.71 |  | 38.71 | 4 | 4
88 |  | 220/132 KV SS Mahabubnagar (Bhoothpur) | 3*160 | 480 | 220KV | 456 | 228 |  | 228 | 0 | 0
[5 empty] | 132KV |  | 228 |  | 228 | 0 | 0
|  |  | 1*31.5+1*50 | 81.5 | 33KV | 77.425 | 38.7125 |  | 38.7125 | 3 | 2
89 |  | 220 /132/33 KV SS Kosgi (Automation) | 2*100 | 200 | 220KV | 190 | 95 |  | 95 | 1 | 2
[5 empty] | 132KV |  | 95 |  | 95 | 2 | 2
|  |  | 1*31.5+1*50 | 81.5 | 33KV | 73.35 | 36.675 | 10 | 26.675 | 3 | 4
90 |  | 220/132 KV SS Thimmajipet (Automation) | 1*100 | 100 | 220KV | 95 | 47.5 |  | 47.5 | 4 | 0
[5 empty] | 132KV |  | 47.5 |  | 47.5 | 0 | 0
91 |  | 132/33 KV SS Mahabubnagar | 2*50+1*80 | 180 | 132KV | 171 | 85.5 |  | 85.5 | 0 | 0
[5 empty] | 33KV |  | 85.5 |  | 85.5 | 2 | 2
92 |  | 132/33 KV SS Narayanpet | 2*31.5 | 63 | 132KV | 59.85 | 29.925 |  | 29.925 | 0 | 2
[5 empty] | 33KV |  | 29.93 |  | 29.93 | 1 | 4
93 |  | 132/33 KV SS Balanagar | 2*80+1*50 | 210 | 132KV | 199.5 | 99.75 | 50 | 49.75 | 0 | 3
[5 empty] | 33KV |  | 99.75 |  | 99.75 | 0 | 0
94 |  | 132/33 KV SS Jadcherla (Automation) | 2*50 | 100 | 132KV | 95 | 47.5 | 40 | 7.5 | 0 | 2
[5 empty] | 33KV |  | 47.5 | 5 | 42.5 | 3 | 3
95 |  | 132/33 KV SS Midjil (Automation) | 2*31.5 | 63 | 132KV | 59.85 | 29.925 |  | 29.925 | 0 | 2
[5 empty] | 33KV |  | 29.93 | 25 | 4.93 | 2 | 4
96 |  | 132/33 KV SS Maddur | 1*50+2*31.5 | 113 | 132KV | 107.35 | 53.675 | 30 | 23.675 | 0 | 2
[5 empty] | 33KV |  | 53.68 |  | 53.68 | 1 | 4
97 |  | 132/33 KV SS Marikal | 3*31.5 | 94.5 | 132KV | 89.775 | 44.8875 |  | 44.8875 | 1 | 0
[5 empty] | 33KV |  | 44.89 | 25 | 19.89 | 0 | 0
98 |  | 132/33 KV SS Makthal | 1*50+2*31.5 | 113 | 132KV | 107.35 | 53.675 |  | 53.675 | 0 | 2
[5 empty] | 33KV |  | 53.68 | 15 | 38.68 | 2 | 2
99 |  | 400/220 KV SS Dindi (Automation) | 2*315 | 945 | 400KV | 897.75 | 448.875 |  | 448.875 | 0 | 4
[5 empty] | 220KV |  | 448.875 |  | 448.875 | 0 | 0
100 |  | 220/132 KV SS Kalwakurthy | 2*160+100 | 420 | 220KV | 399 | 199.5 | 100 | 99.5 | 0 | 0
[5 empty] | 132KV |  | 199.5 |  | 199.5 | 0 | 0
101 |  | 220/33 KV SS Domalapenta (Automation) | 2*31.5 | 63 | 220KV | 59.85 | 29.925 |  | 29.925 | 0 | 0
[5 empty] | 33KV |  | 29.93 |  | 29.93 | 0 | 2
102 |  | 220/132/33 KV SS Nagarkurnool | 2*100 | 200 | 220KV | 190 | 95 |  | 95 | 0 | 2
[5 empty] | 132KV |  | 95 |  | 95 | 0 | 1
|  |  | 2*50+1*31.5 | 131.5 | 33KV | 124.925 | 62.4625 | 35 | 27.4625 | 0 | 3
103 |  | 220/132 KV SS Gouridevipally (Miion Bhageeratha) (Automation) | 2*50 | 100 | 220KV | 95 | 47.5 |  | 47.5 | 0 | 2
[5 empty] | 132KV |  | 47.5 |  | 47.5 | 0 | 0
104 |  | 132/33 KV SS Kalwakurthy | 3*50 | 150 | 132KV | 142.5 | 71.25 |  | 71.25 | 0 | 0
[5 empty] | 33KV |  | 71.25 | 30 | 41.25 | 2 | 0
105 |  | 132/33 KV SS Achampet | 1*80+1*50 | 130 | 132KV | 123.5 | 61.75 |  | 61.75 | 0 | 2
[5 empty] | 33KV |  | 61.75 | 30 | 31.75 | 0 | 0
106 | Metro-Cental | 220 KV GISS OU | 160 | 320 | 220kV | 304 | 152 | 0 | 152 | 132 KV bays 2 Nos (proposed for 132KV OU- ZTS Moulali feeder circuits -1 & 2) | 220 KV 2 Nos, 132 KV 4 Nos and 33 KV 2 Nos
|  |  | 160 |  | 132kV |  | 152 | 0 | 152
|  |  | 80 | 160 | 33kV | 152 | 76 | 0 | 76
80
107 |  | 220 KV GISS Chanchalguda | 50 | 150 | 220kV | 142.5 | 71.25 | 0 | 71.25 | 2Nos. (220KV level) | Space available for One 220KV Module and One 33KV Module
|  |  | 50 |  | 33kV |  | 71.25 | 0 | 71.25
50
108 |  | 132 KV GISS Fever hospital | 80 | 160 | 132kV | 152 | 76 | 0 | 76 | 2Nos. 33KV bays available out of which one bay allotted to TGRTC | Space available for One 132KV feeder bay Module
|  |  | 80 |  | 33kV |  | 76 | 0 | 76
109 |  | 132 KV GISS Narayanaguda | 50 | 100 | 132kV | 95 | 47.5 | 0 | 47.5 | 1No. 132KV level | No space available
|  |  | 50 |  | 33kV |  | 47.5 | 0 | 47.5
110 |  | 132 KV GISS Moosarambagh | 80-1 | 160 | 132kV | 152 | 76 | 0 | 76 | 1No.132KV level | Yes
|  |  | 80-2 |  | 33kV |  | 76 | 0 | 76
111 |  | 132KV Erragadda SS | 80-I | 240 | 132kV | 228 | 114 | 0 | 114 | NIL | Space available for 2os.33KV feeder bays and 1No.PTR bay
|  |  | 80-II |  | 33kV |  | 114 | 0 | 114
80-III
112 |  | 220KV GIS SS Erragadda | 160-I | 480 | 220kV | 456 | 228 | 0 | 228 | 1No. 220KV bay (Proposed 220KV feeder from Raidurg) | Space available for 1No.220KV , 1No.132KV bay
|  |  | 160-II |  | 132kV |  | 228 | 0 | 228
160-III
113 |  | 132KV SS JubileeHills | 80 | 260 | 132kV | 247 | 123.5 | 0 | 123.5 | NIL | Not Available
|  |  | 80 |  | 33kV |  | 123.5 | 0 | 123.5
50
50
114 |  | 132KV SS Madhapur | 80 | 240 | 132kV | 228 | 114 | 0 | 114 | Nil | Not Available
|  |  | 80 |  | 33kV |  | 114 | 0 | 114
80
115 |  | 132KV GIS Hussainsagar | 80 | 130 | 132kV | 123.5 | 61.75 | 0 | 61.75 | Nil | Not Available
|  |  | 50 |  | 33kV |  | 61.75 | 0 | 61.75
116 |  | 132kV GIS Chilkalguda | 50 | 100 | 132kV | 95 | 47.5 | 0 | 47.5 | Nil | Not Available
|  |  | 50 |  | 33kV |  | 47.5 | 0 | 47.5
117 |  | 132KV GISS NIMS | 80 | 160 | 132kV | 152 | 76 | 0 | 76 | Nil | Not Available
|  |  | 80 |  | 33kV |  | 76 | 0 | 76
118 |  | 220KV SS GUNROCK | 160 | 480 | 220kV | 456 | 228 | 0 | 228 | NIL | Available Proposal was sent for providing alteranate sources to 220KV SS Gunrock vide Lr.No.SE/OMC/Metro-Central/Hyd/ADE(T)/AE1/F./D.No.4892/24, Dt:25.01.2025
|  |  | 160 |  | 132kV |  | 228 | 0 | 228
160
119 |  | 132KV SS GUNROCK | 80 | 260 | 132kV | 247 | 123.5 | 0 | 123.5 | NIL | Not Available
|  |  | 80 |  | 33kV |  | 123.5 | 0 | 123.5
50
50
120 |  | 132 KV GIS PATIGADDA | 80 | 130 | 132kV | 123.5 | 61.75 | 0 | 61.75 | 132KV -1No. (Proposed for a feeder to 132KV GIS NIMS) | Not Available
|  |  | 50 |  | 33kV |  | 61.75 | 0 | 61.75
121 |  | 132 KV GIS BALKAMPET | 80 | 160 | 132kV | 152 | 76 | 0 | 76 | NIL | Not Available
|  |  | 80 |  | 33kV |  | 76 | 0 | 76
122 |  | 132KV SS Imlibun | 80 | 240 | 132kV | 228 | 114 | 0 | 114 | NIL | Not Available
|  |  | 80 |  | 33kV |  | 114 | 0 | 114
80
123 |  | 220KV GISS Imlibun | 160 | 320 | 220kV | 304 | 152 | 0 | 152 | 220KV- NIL 132KV- 3Nos (Out of three Nos. two are proposed for PTO SubStations) | Not Available
|  |  | 160 |  | 132kV |  | 152 | 0 | 152
124 |  | 132KV SS Asif Nagar | 80 | 160 | 132KV | 152 | 76 | 0 | 76 | NIL | Not Available
|  |  | 80 |  | 33KV |  | 76 | 0 | 76
125 |  | 132KV GIS Manikonda | 80 | 160 | 132KV | 152 | 76 | 0 | 76 | 5 no(33 kv) bays available.Requests received from 13 Nos. HT consumers. 2 Nos. 132 kv feede bays available. LILO of 132KV Chandrayangutta -Jubileehills feeder is proposed | Space available for 3Nos. 33KV bays (GIS Modules)
|  |  | 80 |  | 33KV |  | 76 | 0 | 76
126 | Metro-East | 400KV Maheshwaram | 500MVA ICT-I | 1000 | 400 | 950 | 475 | 0 | 475 | 0 | available
|  |  | 500MVA ICT-II |  | 220 |  | 475 | 0 | 475 | 0 | available
127 |  | 400KV SS Malkaram | 315MVA ICT-1 | 1260 | 400 | 1197 | 598.5 | 0 | 598.5 | 0 | -
|  |  | 315MVA ICT-2 |  | 220 |  | 598.5 | 0 | 598.5 | 5 | available
|  |  | 315MVA ICT-3 | [5 empty] | 0
|  |  | 315MVA ICT-4 | [5 empty] | 0
|  |  | 100MVA PTR-I | 260 | 132 | 247 | 123.5 | 19.8 | 103.7 | 1
|  |  | 160MVA PTR-2 | [5 empty] | 0
|  |  | 80MVA PTR-I | 160 | 33 | 152 | 76 | 0 | 76 | 0
|  |  | 80MVA PTR-2 | [5 empty] | 0
128 |  | 400 /220KV Mamidipally SS | 315 MVA ICT-I | 1260 | 400 | 1197 | 598.5 | 0 | 598.5 | 1 | available
|  |  | 315 MVA ICT-II |  | 220 |  | 598.5 | 0 | 598.5 | 0 | available
|  |  | 315 MVA ICT-III | [5 empty] | 0
|  |  | 315 MVA ICT-IV | [5 empty] | 0
129 |  | 220 KV Bonguluru | 100MVA PTR-I | 200 | 220 | 190 | 95 | 0 | 95 | 0 | available for1 bay
|  |  | 100MVA PTR-II |  | 132 |  | 95 |  | 95
|  |  | 50MVA PTR-I | 81.5 | 33 | 77.425 | 38.7125 | 0 | 38.7125 | 0 | available for1 bay
|  |  | 31.5MVA PTR-II | [5 empty] | 0
130 |  | 220KV SS Moulali | 160 MVA PTR-I | 420 | 220 | 399 | 199.5 | 0 | 199.5 | 0 | Available
|  |  | 160 MVA PTR-II |  | 132 |  | 199.5 | 0 | 199.5 | 1 | Available
|  |  | 100 MVA PTR-III | [5 empty] | 0
|  |  | 80MVA PTR-II | 240 | 33 | 228 | 114 | 0 | 114 | 0 | Available
|  |  | 80MVA PTR-III | [5 empty] | 0
|  |  | 80MVA PTR-IV | [5 empty] | 0
131 |  | 220KV SS Nagole | 100MVA PTR-I | 200 | 220 | 190 | 95 | 0 | 95 | 2 | Not Available
|  |  | 100MVA PTR-II |  | 132 |  | 95 | 0 | 95 | 0 | Not Available
|  |  | 31.5MVA PTR | 111.5 | 33 | 105.925 | 52.9625 | 0 | 52.9625 | 0 | Not Available
|  |  | 80MVA PTR-I | [5 empty] | 0
132 |  | 220KV SS Ghanapur | 100MVA PTR-I | 420 | 220 | 399 | 199.5 | 0 | 199.5 | 0 | Not available
|  |  | 160MVA PTR-II |  | 132 |  | 199.5 | 0 | 199.5 | 1 | Not available
|  |  | 160MVA PTR-III | [5 empty] | 0
|  |  | 50MVA PTR-I | 130 | 33 | 123.5 | 61.75 | 0 | 61.75 | 1 | Available
|  |  | 80MVA PTR-II | [5 empty] | 0
133 |  | 220/33 KV HIAL SS | 50 MVA PTR-I | 100 | 220 | 95 | 47.5 | 0 | 47.5 | 0 | Not available
|  |  | 50 MVA PTR-II |  | 33 |  | 0 | 0 | 0 | 0 | -
134 |  | 220/33 KV GHIAL SS | 25 MVA PTR-I | 50 | 220 | 47.5 | 23.75 | 0 | 23.75 | - | -
|  |  | 25 MVA PTR-II |  | 33 |  | 23.75 | 0 | 23.75 | - | -
135 |  | 220/132/33KV Fabcity SS | 100MVA PTR-I | 200 | 220 | 190 | 95 | 0 | 95 | 0 | Available
|  |  | 100MVA PTR-II |  | 132 |  | 95 | 0 | 95 | 0 | Available
|  |  | 50 MVA PTR-I | 100 | 33 | 95 | 47.5 | 0 | 47.5 | 1 | Available
|  |  | 50 MVA PTR-II | [5 empty] | 0
136 |  | 220/132/33 KV Shamshabad SS | 100 MVA -I | 200 | 220 | 190 | 95 | 0 | 95 | 2 | not available
|  |  | 100 MVA -III |  | 132 |  | 95 | 0 | 95 | 3 | not available
|  |  | 50MVA-I | 100 | 33 | 95 | 47.5 | 0 | 47.5 | 1 | not available
|  |  | 50 MVA -II | [5 empty] | 0
137 |  | 220 KV Chandrayanagutta | 160MVA-I | 480 | 220 | 456 | 228 | 0 | 228 | 0 | Available for 1 bay
|  |  | 160MVA-II |  | 132 |  | 228 | 0 | 228 | 0 | Available for 2 bay
|  |  | 160MVA -III | [5 empty] | 0
|  |  | 50MVA -I | 230 | 33 | 218.5 | 109.25 | 0 | 109.25 | 0 | Available for 2 bay
|  |  | 50MVA -II | [5 empty] | 0
|  |  | 50MVA -III | [5 empty] | 0
|  |  | 80MVA -IV | [5 empty] | 0
138 |  | 220KV SS Hayathnagar | 100MVA-I | 200 | 220 | 190 | 95 | 0 | 95 | 0 | Available for 2 bay
|  |  | 100MVA-II |  | 33 |  | 95 | 0 | 95 | 0 | Available for 8 bay
139 |  | 220KVSS Shivarampally | 160MVA PTR-I | 520 | 220 | 494 | 247 | 0 | 247 | 0 | 0
|  |  | 100MVA PTR-II |  | 132 |  | 247 | 0 | 247 | 1 | 0
|  |  | 100MVA PTR-III | [5 empty] | 0
|  |  | 160MVA PTR-IV | [5 empty] | 0
|  |  | 50MVA PTR-I | 340 | 33 | 323 | 161.5 | 0 | 161.5 | 0 | Available for 2 bay
|  |  | 80MVA PTR-II | [5 empty] | 0
|  |  | 50MVA PTR-III | [5 empty] | 0
|  |  | 80MVA PTR-IV | [5 empty] | 0
|  |  | 80MVA PTR-V | [5 empty] | 0
140 |  | 220/132/33 KV Madgula SS | 100 MVA PTR-1 | 200 | 220 | 190 | 95 | 0 | 95 | 0 | 0
|  |  | 100 MVA PTR-2 |  | 132 |  | 95 | 0 | 95 | 1 | Available for 2 bay
|  |  | 31.5 MVA PTR -I | 63 | 33 | 59.85 | 29.925 | 0 | 29.925 | 0 | 0
|  |  | 31.5 MVA PTR -II | [5 empty] | 0
141 |  | 220/132/33 KV SS SHADNAGAR | 160MVA PTR-III | 360 | 220 | 342 | 171 | 0 | 171 | 2 | available
|  |  | 100 MVA PTR-I |  | 132 |  | 171 | 0 | 171 | 1 | no
|  |  | 100 MVA PTR-II | [5 empty] | 0
|  |  | 80 MVA PTR-I | 130 | 33 | 123.5 | 61.75 | 0 | 61.75 | 4 | available
|  |  | 50 MVA PTR-II | [5 empty] | 0
142 |  | 220/132/33 KV SS CHEGUR | 160 MVA PTR-I | 320 | 220 | 304 | 152 | 0 | 152 | 1 | available
|  |  | 160 MVA PTR-II |  | 132 |  | 152 | 0 | 152 | 1 | available
|  |  | 80 MVA PTR-II | 80 | 33 | 76 | 38 | 0 | 38 | 4 | available
143 |  | 132/33 KV SS KOTHUR | 50MVA PTR-I | 180 | 132 | 171 | 85.5 | 0 | 85.5 | 0 | no
|  |  | 50MVA PTR-II |  | 33 |  | 85.5 | 0 | 85.5 | 0 | no
|  |  | 80MVA PTR | [5 empty] | 0
144 |  | 132/33 KV SS ALWAL | 31.5MVA PTR-I | 63 | 132 | 59.85 | 29.925 | 0 | 29.925 | 1 | available
|  |  | 31.5MVA PTR-II |  | 33 |  | 29.93 | 0 | 29.93 | 2 | available
145 |  | 132 kV Turkayamjal | 80MVA PTR-I | 130 | 132 | 123.5 | 61.75 | 0 | 61.75 | 0 | Available for 1 no 132kv bay
|  |  | 50MVA PTR-II |  | 33 |  | 61.75 | 0 | 61.75 | 0 | Available for 3 no 33kv bays
146 |  | 132 kV Ibrahimpatnam | 50MVA PTR-I | 100 | 132 | 95 | 47.5 | 0 | 47.5 | 0 | Available for 1 no 132kv bay
|  |  | 50MVA PTR-II |  | 33 |  | 47.5 | 0 | 47.5 | 0 | NOT Available
147 |  | 132 kV Takkallapally | 31.5MVA PTR-I | 31.5 | 132 | 29.925 | 14.9625 | 0 | 14.9625 | 0 | available for1 bay
[5 empty] | 33 |  | 14.96 | 0 | 14.96 | 2 | Available for 2 bays
148 |  | 132/33 KV Mamidipally SS | 50 MVA-I | 131.5 | 132 | 124.925 | 62.4625 | 0 | 62.4625 | 0 | not available
|  |  | 31.5 MVA-II |  | 33 |  | 62.46 | 0 | 62.46 | 3 | not available
|  |  | 50 MVA-III | [5 empty] | 0
149 |  | 132 kV Bandlaguda | 80MVA PTR-I | 160 | 132 | 152 | 76 | 0 | 76 | 0 | 0
|  |  | 80MVA PTR-II |  | 33 |  | 76 | 0 | 76 | 0 | Available for 2 bays
150 |  | 132 KV SS Md'pally | 50 MVA PTR-I | 180 | 132 | 171 | 85.5 | 0 | 85.5 | 0 | 0
|  |  | 50 MVA PTR-II |  | 33 |  | 85.5 | 0 | 85.5 | 0 | Available for 2 bays
|  |  | 80 MVA-III | [5 empty] | 0
151 |  | 132/33 KV Amangal SS | 50 MVA PTR -I | 113 | 132 | 107.35 | 53.675 | 0 | 53.675 | 0 | Available for 2 bays
|  |  | 31.5 MVA PTR -II |  | 33 |  | 53.68 | 12.2 | 41.48 | 1 | Available for 1 bay
31.5 MVA PTR -III
152 |  | 132KV SS LGMPET | 50MVA PTR-I | 130 | 132 | 123.5 | 61.75 | 0 | 61.75 | 1 | -
|  |  | 80MVA PTR-II |  | 33 |  | 61.75 | 0 | 61.75 | 0 | -
153 |  | 132KV SS ZTS Moulali | 50MVA PTR-I | 130 | 132 | 123.5 | 61.75 | 0 | 61.75 | 0 | available
|  |  | 80MVA PTR-II |  | 33 |  | 61.75 | 0 | 61.75 | 0 | available
154 |  | 132KV SS E-City | 80MVA PTR-I | 80 | 132 | 76 | 38 | 0 | 38 | 0 | available
[5 empty] | 33 |  | 38 | 0 | 38 | 7 | available
155 | Metro-West | 400KV GISS Raidurg | 2x500 | 1000 | 400KV | 950 | 475 | 0 | 475 | Nil | Yes
[5 empty] | 220KV |  | 475 | 0 | 475 | Nil
|  |  | 2x160 | 320 | 132KV | 304 | 152 | 0 | 152 | Nil
|  |  | 3x80 | 240 | 33KV | 228 | 114 | 0 | 114 | 2
156 |  | 132KV SS Medchal | 180 | 180 | 132KV | 171 | 85.5 | 0 | 85.5 | Nil | Nil
[5 empty] | 33KV |  | 85.5 | 0 | 85.5
157 |  | 132KV SS Chintal | 1 x 80+ 1x 50 | 130 | 132KV | 123.5 | 61.75 | 0 | 61.75 | 132KV-2 | 33KV-2
[5 empty] | 33KV |  | 61.75 | 0 | 61.75
158 |  | 132KV SS Khaithalapur | 2x80 | 160 | 132 Kv | 152 | 76 | 0 | 76 | 132 KV -2 | Land available for upgradation of 132 KVSS to 220 KVSS
[5 empty] | 33 KV |  | 76 | 0 | 76 | 33 KV - 2
159 |  | 220KV SS Medchal | 480 | 480 | 220 | 456 | 228 | 0 | 228 | nil | Yes
[5 empty] | 132 |  | 228 | 0 | 228 | 132kV -1
160 |  | 220KV SS Miyapur | 2x 160 | 320 | 220KV | 304 | 152 | 0 | 152 |  | 220KV -1
[5 empty] | 132KV |  | 152 | 0 | 152
161 |  | 132KV Gachibowli | 2x80 | 160 | 132KV | 152 | 76 | 0 | 76 | nil | nil
[5 empty] | 33KV |  | 76 | 0 | 76
162 |  | 220kv gachibowli | 4x160 | 640 | 220KV | 608 | 304 | 0 | 304 | nil | nil
[5 empty] | 132KV |  | 304 | 0 | 304 | 132 KV -2 | nil
|  |  | 2x50+2x80 | 260 | 33KV | 247 | 123.5 | 0 | 123.5
163 |  | 132 KVSS RC Puram | 1x50 + 2*80 | 210 | 132 | 199.5 | 99.75 | 0 | 99.75 | 33 KV - 3 | available and proposed for bay extension at 33kv level
[5 empty] | 33 |  | 99.75 | 1 | 98.75
164 |  | 132 KVSS Dharmasagar | 2X31.5 | 94.5 | 132 | 89.775 | 44.8875 | 0 | 44.8875 | Nil | Land Available for future expansion
[5 empty] | 33 |  | 44.89 | 4 | 40.89 | Nil
165 |  | 132 KVSS DP Pally | 2x31.5 | 63 | 132 | 59.85 | 29.925 | 0 | 29.925 | 1 no.33kv bay with equipment and 1no.spare 33kv bay available | Land available for 2nos 33 kV bays
[5 empty] | 33 |  | 29.93 | 0 | 29.93
166 |  | 220 KVSS Shapurnagar | 3×160 | 480 | 220 | 456 | 228 | 0 | 228 | nil | yes
[5 empty] | 132 |  | 228 | 0 | 228 | nil | yes
|  |  | 3×80 | 240 | 33 | 228 | 114 | 0 | 114 | nil
167 |  | 132 KVSS IDPL | 1 x 80+ 1x 50 | 130 | 132KV | 123.5 | 61.75 | 0 | 61.75 | Nil | Nil
[5 empty] | 33KV |  | 61.75 | 0 | 61.75
168 |  | 132 KV Kanakamamidi SS | 1X80 | 80 | 132KV | 76 | 38 | 0 | 38 | 33 KV -2 spare bays available | Land Available for future expansion
[5 empty] | 33KV |  | 38 | 0 | 38
169 |  | 132kV Donthanpally SS | 1X80+1×50 | 130 | 132KV | 123.5 | 61.75 | 0 | 61.75 | 132KV -2 No & 33kV -2 No. | Available for 132kV & 33kV future expansion
[5 empty] | 33KV |  | 61.75 | 0 | 61.75
170 |  | 220 KV Chandanvally SS | 1X100 | 100 | 220KV | 95 | 47.5 | 0 | 47.5 | 33 KV - 3 spare bays available | Land Available for future expansion
[5 empty] | 132KV |  | 47.5 | 0 | 47.5
|  |  | 2x50 | 100 | 132kV | 95 | 47.5 | 0 | 47.5
[5 empty] | 33KV |  | 47.5 | 0 | 47.5
171 |  | 132kvss vikarabad | 2*16 | 32 | 132kv | 30.4 | 15.2 | 0 | 15.2 | 33kv-3 no of spare bays | nill
[5 empty] | 33KV |  | 15.2 | 10 | 5.2
172 |  | 132KV SS Kodangal | 3*31.5 | 63 | 132KV | 59.85 | 29.925 | 0 | 29.925 |  | Yes
[5 empty] | 33KV |  | 29.93 | 18 | 11.93 | 1
173 |  | 220KV SS Tandur | 2*100 | 200 | 220KV | 190 | 95 | 0 | 95 | Nil | Yes
[5 empty] | 132KV |  | 95 | 50 | 45
|  |  | 2*50 | 100 | 33KV | 95 | 47.5 | 15 | 32.5 | 33KV-2 spare bays available
174 |  | 400kV SS Kethireddypally | 2x315 | 630 | 400kV | 598.5 | 299.25 | 0 | 299.25 | 2no.220kV & 2 no.132kV spare bays available | For 132kV & 220kV Bays available
[5 empty] | 220kV |  | 299.25 |  | 299.25
|  |  | 1X100 | 100 | 132KV | 95 | 47.5 | 0 | 47.5
175 |  | 400kV Shankarpally | 1*500 + 3*315 | 1445 | 400kV | 1372.75 | 686.375 | 0 | 686.375 | 400kV - 3 No | Land Available for future expansion
[5 empty] | 220KV |  | 686.38 | 0 | 686.38
176 |  | 220KV SS Parigi | 2*100 | 200 | 220KV | 190 | 95 | 0 | 95 | NIL | For 132kV 1 NO BAY & FOR 220kV 2NO'S Bays available
[5 empty] | 132KV |  | 95 | 100.8 | -5.8
177 |  | 132KV SS Puttapahad | 3*31.5 | 94.5 | 132KV | 89.775 | 44.8875 | 0 | 44.8875 | NIL | NIL
[5 empty] | 33KV |  | 44.89 | 0 | 44.89
178 |  | 132KVSS Parigi | 2*50 | 100 | 132KV | 95 | 47.5 | 0 | 47.5 | NIL | NIL
[5 empty] | 33KV |  | 47.5 | 15 | 32.5 | 33KV -1 SPARE BAY AVAILABLE
179 |  | 132KVSS Srirangapur | 1*31.5+1*50 | 81.5 | 132KV | 77.425 | 38.7125 | 0 | 38.7125 | 33KV -2NO SPARE BAY AVAILABLE | For 132kV & 33kV Bays available
[5 empty] | 33KV |  | 38.71 | 0 | 38.71
180 | Nalgonda | 400/220/132 KV SS Choutuppal | 2 X 500 | 1000 | 400 KV | 950 | 475 | 0 | 475 | 2 | 2
[5 empty] | 220 KV |  | 475 | 0 | 475 | 4 | 2
|  |  | 2 X 160 | 320 | 132 KV | 304 | 152 | 0 | 152 | 4 | 0
181 |  | 220 KV SS Narketpally | 2 X 100 + 2 X 160 | 520 | 220 KV | 494 | 247 | 100 | 147 | 3 | 0
[5 empty] | 132 KV |  | 247 | 0 | 247 | 1 | 1
|  |  | 1 X 31.5 + 1 X 50 | 81.5 | 33 KV | 77.425 | 38.71 | 0 | 38.71 | 3 | 1
182 |  | 220 KV SS Bhongir | 3 X 100 | 300 | 220 KV | 285 | 142.5 | 50 | 92.5 | 2 | 0
[5 empty] | 132 KV |  | 142.5 | 0 | 142.5 | 2 | 0
|  |  | 1 X 80 + 1 X 50 | 130 | 33 KV | 123.5 | 61.75 | 0 | 61.75 | - | 0
183 |  | 132 KV SS Nalgonda | 1 X 80 + 1 X 50 + 1 X 31.5 | 161.5 | 132 KV | 153.425 | 76.7125 | 0 | 76.7125 | 1 | 0
[5 empty] | 33 KV |  | 76.71 | 0 | 76.71 | 2 | 0
184 |  | 132 KV SS Kolanpaka | 1 X 80 + 2 X 50 | 180 | 132 KV | 171 | 85.5 | 0 | 85.5 | - | 0
[5 empty] | 33 KV |  | 85.5 | 31 | 54.5 | - | 0
185 |  | 132 KV SS Bibinagar | 1 X 80 + 1 X 50 | 130 | 132 KV | 123.5 | 61.75 | 0 | 61.75 | - | 0
[5 empty] | 33 KV |  | 61.75 | 13 | 48.75 | - | 0
186 |  | 132 KV SS Yadagirigutta | 2 X 31.5 | 63 | 132 KV | 59.85 | 29.925 | 0 | 29.925 | - | 0
[5 empty] | 33 KV |  | 29.93 | 0 | 29.93 | 2 | 0
187 |  | 132 KV SS Ramannapet | 3 X 50 | 150 | 132 KV | 142.5 | 71.25 | 0 | 71.25 | - | 1
[5 empty] | 33 KV |  | 71.25 | 45 | 26.25 | - | 0
188 |  | 132 KV SS Shaligowraram | 1 X 80 + 1 X 50 | 130 | 132 KV | 123.5 | 61.75 | 0 | 61.75 | - | 2
[5 empty] | 33 KV |  | 61.75 | 0 | 61.75 | - | 1
189 |  | 132 KV SS Choutuppal | 3 X 50 | 150 | 132 KV | 142.5 | 71.25 | 0 | 71.25 | - | 0
[5 empty] | 33 KV |  | 71.25 | 0 | 71.25 | - | 0
190 |  | 132 KV SS Mothkur | 2 X 50 | 100 | 132 KV | 95 | 47.5 | 0 | 47.5 | - | 1
[5 empty] | 33 KV |  | 47.5 | 14 | 33.5 | - | 0
191 |  | 132 KV SS Kanagal | 2 X 50 | 100 | 132 KV | 95 | 47.5 | 0 | 47.5 | - | 4
[5 empty] | 33 KV |  | 47.5 | 0 | 47.5 | 4 | 4
192 |  | 132 KV SS Aitipamula | 1 X 80 + 1 X 31.5 | 111.5 | 132 KV | 105.925 | 52.9625 | 0 | 52.9625 | - | 1
[5 empty] | 33 KV |  | 52.96 | 15 | 37.96 | - | 1
193 |  | 132 KV SS Yerrabelly | 2 X 50 | 100 | 132 KV | 95 | 47.5 | 0 | 47.5 | - | 1
[5 empty] | 33 KV |  | 47.5 | 0 | 47.5 | 2 | 3
194 |  | 132 KV SS Munugodu | 2 X 31.5 | 63 | 132 KV | 59.85 | 29.925 | 0 | 29.925 | - | 1
[5 empty] | 33 KV |  | 29.93 | 0 | 29.93 | 1 | 1
195 |  | 400 KV SS Damaracherla | 2 X 500 | 1000 | 400 KV | 950 | 475 | 0 | 475 | - | 2
[5 empty] | 220 KV |  | 475 | 0 | 475 | - | 0
196 |  | 220 KV SS Miryalaguda. | 2 X 160 + 2 X 100 | 520 | 220 KV | 494 | 247 | 0 | 247 | - | 0
[5 empty] | 132 KV |  | 247 | 0 | 247 | - | 1
|  |  | 2 X 80 | 160 | 33 KV | 152 | 76 | 0 | 76 | - | 0
197 |  | 220 KV SWS Chalakurthy. | SWS |  | 220 KV |  | 0 | 0 | 0 | - | 5
198 |  | 220 KV SS KMPally. | 4 X 100 | 400 | 220 KV | 380 | 190 | 0 | 190 | - | 2
[5 empty] | 132 KV |  | 190 | 148 | 42 | 3 | 0
199 |  | 132 KV SS Wadapally | 1 X 31.5 & 1 X 50 | 81.5 | 132 KV | 77.425 | 38.7125 | 0 | 38.7125 | 2 | 0
[5 empty] | 33 KV |  | 38.71 | 0 | 38.71 | - | 2
200 |  | 132 KV SWS Ganeshpahad | SWS |  | 132 KV |  | 0 | 0 | 0 | 2 | 0
201 |  | 132 KV SS Dirsincherla | 2 X 50 | 100 | 132 KV | 95 | 47.5 | 0 | 47.5 | - | 0
[5 empty] | 33 KV |  | 47.5 | 0 | 47.5 | - | 1
202 |  | 132 KV SS Guntipally | 2 X 31.5 + 1 X 10/16 | 79 | 132 KV | 75.05 | 37.525 | 0 | 37.525 | 1 | 1
[5 empty] | 33 KV |  | 37.53 | 15 | 22.53 | 5 | 0
203 |  | 132 KV SS KMPally | 1 X 50 + 1 X 31.5 + 1 X 80 | 161.5 | 132 KV | 153.425 | 76.7125 | 0 | 76.7125 | - | 0
[5 empty] | 33 KV |  | 76.71 | 0 | 76.71 | - | 0
204 |  | 132 KV SWS Nasarlapally | SWS |  | 132 KV |  | 0 | 0 | 0 | - | 2
205 |  | 132 KV SWS Godakondla | SWS |  | 132 KV |  | 0 | 0 | 0 | - | 2
206 |  | 132 KV SS Haliya | 2 X 50 | 100 | 132 KV | 95 | 47.5 | 0 | 47.5 | - | 0
[5 empty] | 33 KV |  | 47.5 | 0 | 47.5 | 1 | 0
207 |  | 132 KV SWS Kodandapur | 2 X 31.5 | 63 | 132 KV | 59.85 | 29.925 | 0 | 29.925 | - | 2
[5 empty] | 33 KV |  | 29.93 | 0 | 29.93 | 2 | 2
208 |  | 132 KV SS Madgulapally | 1 X 80 +1 X 50 | 130 | 132 KV | 123.5 | 61.75 | 0 | 61.75 | - | 0
[5 empty] | 33 KV |  | 61.75 | 2.5 | 59.25 | - | 0
209 |  | 132 KV SS Marriguda | 2 X 50 + 1 X 31.5 | 131.5 | 132 KV | 124.925 | 62.4625 | 0 | 62.4625 | 1 | 1
[5 empty] | 33 KV |  | 62.46 | 0 | 62.46 | 1 | 1
210 |  | 400 KV SS Suryapet | 2 X 315 + 1 X 500 | 1130 | 400 KV | 1073.5 | 536.75 | 0 | 536.75 | 1 | 2
[5 empty] | 220 KV |  | 536.75 | 0 | 536.75 | - | 5
|  |  | 1 X 100 + 2 X 160 | 420 | 132 KV | 399 | 199.5 | 0 | 199.5 | 1 | 5
211 |  | 220 KV SS Sithapuram | 2 X 100 | 200 | 220 KV | 190 | 95 | 0 | 95 | - | 2
[5 empty] | 132 KV |  | 95 | 0 | 95 | 3 | 1
212 |  | 220 KV SS Huzurnagar | 2 X 100 | 200 | 220 KV | 190 | 95 | 0 | 95 | - | 2
[5 empty] | 132 KV |  | 95 | 0 | 95 | - | 4
|  |  | 2 X 31.5 | 63 | 33 KV | 59.85 | 29.925 | 0 | 29.925 | 2 | 4
213 |  | 132 KV SS Suryapet | 3 X 80 | 240 | 132 KV | 228 | 114 | 0 | 114 | - | 2
[5 empty] | 33 KV |  | 114 | 0 | 114 | 2 | 3
214 |  | 132 KV SS Thungaturthy | 2 X 50 | 100 | 132 KV | 95 | 47.5 | 0 | 47.5 | 1 | 0
[5 empty] | 33 KV |  | 47.5 | 15 | 32.5 | - | 2
215 |  | 132 KV SS Kodada | 3 X 50 | 150 | 132 KV | 142.5 | 71.25 | 0 | 71.25 | 1 | 0
[5 empty] | 33 KV |  | 71.25 | 0 | 71.25 | - | 0
216 |  | 132 KV SS Munagala | 2 X 31.5 + 1 X 50 | 113 | 132 KV | 107.35 | 53.675 | 0 | 53.675 | - | 1
[5 empty] | 33 KV |  | 53.68 | 0 | 53.68 | - | 1
217 |  | 132 KV SS Ramapuram | 2 X 31.5 | 63 | 132 KV | 59.85 | 29.925 | 0 | 29.925 | - | 1
[5 empty] | 33 KV |  | 29.93 | 0 | 29.93 | 2 | 4
218 |  | 132 KV SS Mattampally | 2 X 50 | 100 | 132 KV | 95 | 47.5 | 0 | 47.5 | - | 2
[5 empty] | 33 KV |  | 47.5 | 0 | 47.5 | 1 | 0
219 |  | 132 KV SS Nagaram | 1 X 10/16 + 1 X 31.5 | 47.5 | 132 KV | 45.125 | 22.5625 | 0 | 22.5625 | - | 0
[5 empty] | 33 KV |  | 22.56 | 0 | 22.56 | 2 | 0
220 |  | 132 KV SS Nuthankal | 1 X 50 | 50 | 132 KV | 47.5 | 23.75 | 0 | 23.75 | - | 2
[5 empty] | 33 KV |  | 23.75 | 0 | 23.75 | - | 0
221 |  | 132 KV SWS Vepalasingaram | SWS |  | 132 KV |  | 0 | 0 | 0 | - | 2
222 | Nizamabad | 400/220kVSS Dichpally | 3x315+1x500 | 1445 | 400kV | 1372.75 | 686.375 | 0 | 686.375 | - | 6
[5 empty] | 220kV |  | 686.38 | 143 | 543.38 | 2 | 2
223 |  | 220/132 KVSS Bheemgal | 2x160 | 320 | 220kV | 304 | 152 | 0 | 152 | - | 2
[5 empty] | 132kV |  | 152 | 0 | 152 | 1 | 1
|  |  | 2x80 | 160 | 33kV | 152 | 76 | 0 | 76 | - | 2
224 |  | 132KVSS Bussapur. | 1x50+1x31.5 | 81.5 | 132kV | 77.425 | 38.7125 | 0 | 38.7125 | - | 2
[5 empty] | 33kV |  | 38.71 | 0 | 38.71 | - | -
225 |  | 132 KVSS Armoor. | 1x50+1x31.5 | 81.5 | 132kV | 77.425 | 38.7125 | 0 | 38.7125 | - | 3
[5 empty] | 33kV |  | 38.71 | 0 | 38.71 | - | 1
226 |  | 132KVSS Morthad | 1x31.5+ 1x50 | 81.5 | 132kV | 77.425 | 38.7125 | 0 | 38.7125 | - | 1
[5 empty] | 33kV |  | 38.71 | 0 | 38.71 | - | 2
227 |  | 132KVSS Sirikonda | 2x50 | 100 | 132kV | 95 | 47.5 | 0 | 47.5 | - | 1
[5 empty] | 33kV |  | 47.5 | 0 | 47.5 | - | 3
228 |  | 132KVSS Das nagar | 1x50+1x31.5 | 81.5 | 132kV | 77.425 | 38.7125 | 0 | 38.7125 | - | 4
[5 empty] | 33kV |  | 38.71 | 0 | 38.71 | - | 5
229 |  | 220/132 KVSS Dichpally | 3x160+1x100 | 580 | 220kV | 551 | 275.5 | 0 | 275.5 | - | -
[5 empty] | 132kV |  | 275.5 | 0 | 275.5 | - | 3
|  |  | 1x80+1x50 | 130 | 33kV | 123.5 | 61.75 | 0 | 61.75 | - | 1
230 |  | 132/33 KVSS Nizamabad | 3x50 | 150 | 132kV | 142.5 | 71.25 | 0 | 71.25 | - | -
[5 empty] | 33kV |  | 71.25 | 0 | 71.25 | - | 1
231 |  | 132/33 KVSS Nandipet | 2x50 | 100 | 132kV | 95 | 47.5 | 20 | 27.5 | 1 | -
[5 empty] | 33kV |  | 47.5 | 15 | 32.5 | - | 1
232 |  | 132/33 KVSS Bodhan | 1x31.5+ 1x50 | 81.5 | 132kV | 77.425 | 38.7125 | 0 | 38.7125 | - | 7
[5 empty] | 33kV |  | 38.71 | 0 | 38.71 | - | 12
233 |  | 220/132/33 KVSS Renjal | 2x100 | 200 | 220kV | 190 | 95 | 0 | 95 | - | 1
[5 empty] | 132kV |  | 95 | 0 | 95 | - | 3
|  |  | 1x50+1x31.5 | 81.5 | 33kV | 77.425 | 38.71 | 15 | 23.71 | - | -
234 |  | 132/33 KVSS Jakora | 2x50 | 100 | 132kV | 95 | 47.5 | 0 | 47.5 | - | 1
[5 empty] | 33kV |  | 47.5 | 0 | 47.5 | - | -
235 |  | 132/33 KVSS Kotagiri | 3x10/16 | 48 | 132kV | 45.6 | 22.8 | 0 | 22.8 | - | 5
[5 empty] | 33kV |  | 22.8 | 0 | 22.8 | - | 1
236 |  | 220KV SS Kamareddy | 2x100+1x160 | 360 | 220 KV | 342 | 171 | 0 | 171 | - | 1
[5 empty] | 132kV |  | 171 | 134 | 37 | - | 5
237 |  | 220KV SS Banswada | 2x100 | 200 | 220 KV | 190 | 95 | 0 | 95 | 3 | 1
[5 empty] | 132kV |  | 95 | 0 | 95 | - | 2
|  |  | 1x31.5+ 1x50 | 81.5 | 33kV | 77.425 | 38.71 | 0 | 38.71 | - | 1
238 |  | 132KV SS Bhiknoor | 2x31.5 | 63 | 132kV | 59.85 | 29.925 | 0 | 29.925 | - | 2
[5 empty] | 33kV |  | 29.93 | 0 | 29.93 | 2 | -
239 |  | 132KV SS Bichkunda | 2x31.5 | 63 | 132kV | 59.85 | 29.925 | 0 | 29.925 | - | 1
[5 empty] | 33kV |  | 29.93 | 0 | 29.93 | - | 1
240 |  | 132KV SS Domakonda | 2x50 | 100 | 132kV | 95 | 47.5 | 0 | 47.5 | - | 2
[5 empty] | 33kV |  | 47.5 | 15 | 32.5 | - | -
241 |  | 132KV SS Gandimasanipet | 3x10/16 | 48 | 132kV | 45.6 | 22.8 | 0 | 22.8 | - | -
[5 empty] | 33kV |  | 22.8 | 0 | 22.8 | - | 2
242 |  | 132KV SS Kamareddy | 1x50+1x31.5 | 81.5 | 132kV | 77.425 | 38.7125 | 0 | 38.7125 | - | 1
[5 empty] | 33kV |  | 38.71 | 15 | 23.71 | - | 3
243 |  | 132KV SS Lingampet | 1x50+1x31.5 | 81.5 | 132kV | 77.425 | 38.7125 | 0 | 38.7125 | - | 1
[5 empty] | 33kV |  | 38.71 | 15 | 23.71 | - | 1
244 |  | 132KV SS Nizamsagar | 2x31.5 | 63 | 132kV | 59.85 | 29.925 | 16 | 13.925 | - | -
[5 empty] | 33kV |  | 29.93 | 0 | 29.93 | - | 1
245 |  | 132KV SS Padmajiwadi | 2x31.5 | 63 | 132kV | 59.85 | 29.925 | 0 | 29.925 | - | 1
[5 empty] | 33kV |  | 29.93 | 20 | 9.93 | 2 | 1
246 |  | 132KV SS Reddypet | 1x31.5+1x10/16 | 47.5 | 132kV | 45.125 | 22.5625 | 0 | 22.5625 | 1 | -
[5 empty] | 33kV |  | 22.56 | 15 | 7.56 | 3 | 3
247 | Sangareddy | 400/220/132 KV SS Narsapur | 3x315 | 945 | 400kV | 897.75 | 448.875 | 0 | 448.875 | 0 | 0
[5 empty] | 220kV |  | 448.88 | 0 | 448.88 | 0 | 2
|  |  | 2x160+1x100 | 420 | 132kV | 399 | 199.5 | 0 | 199.5 | 2 | 2
248 |  | 220/132/33 KV SS Minpur | 3x160 | 480 | 220kV | 456 | 228 | 65 | 163 | 0 | 0
[5 empty] | 132kV |  | 228 | 100 | 128 | 0 | 0
|  |  | 2x50 | 100 | 33kV | 95 | 47.5 | 0 | 47.5 | 0 | 0
249 |  | 132/33 KV SS Medak | 2x50+1x31.5 | 131.5 | 132kV | 124.925 | 62.4625 | 45 | 17.4625 | 0 | 0
[5 empty] | 33kV |  | 62.46 | 0 | 62.46 | 1 | 2
250 |  | 132/33 KV SS Kowdipally | 1x50+1x16 | 66 | 132kV | 62.7 | 31.35 | 0 | 31.35 | 0 | 0
[5 empty] | 33kV |  | 31.35 | 0 | 31.35 | 0 | 0
251 |  | 132/33 KV SS Narsapur | 2x50 | 100 | 132kV | 95 | 47.5 | 0 | 47.5 | 0 | 0
[5 empty] | 33kV |  | 47.5 | 0 | 47.5 | 0 | 2
252 |  | 132/33 KV SS Peddashankarampet | 2x31.5 | 63 | 132kV | 59.85 | 29.925 | 0 | 29.925 | 0 | 2
[5 empty] | 33kV |  | 29.93 | 10 | 19.93 | 1 | 5
253 |  | 132/33 KV SS Yeldurthy | 2x31.5 | 63 | 132kV | 59.85 | 29.925 | 0 | 29.925 | 0 | 1
[5 empty] | 33kV |  | 29.93 | 0 | 29.93 | 2 | 3
254 |  | 132/33 KV SS Chegunta | 1x80+1x50 | 130 | 132kV | 123.5 | 61.75 | 20 | 41.75 | 0 | 0
[5 empty] | 33kV |  | 61.75 | 15 | 46.75 | 0 | 0
255 |  | 132/33 KV SS Manoharabad | 2x50+1x80 | 180 | 132kV | 171 | 85.5 | 0 | 85.5 | 0 | 0
[5 empty] | 33kV |  | 85.5 | 0 | 85.5 | 0 | 0
256 |  | 132/33 KV SS Ramayampet | 1x50+1x31.5 | 81.5 | 132kV | 77.425 | 38.7125 | 0 | 38.7125 | 0 | 1
[5 empty] | 33kV |  | 38.71 | 10 | 28.71 | 0 | 2
257 |  | 220/132 KV SS Yeddumailaram | 2x160+1x100 | 420 | 220kV | 399 | 199.5 | 0 | 199.5 | 0 | 0
[5 empty] | 132kV |  | 199.5 | 15 | 184.5 | 2 | 1
258 |  | 220/132 KV SS Sadasivapet | 1x100+1x160 | 260 | 220kV | 247 | 123.5 | 0 | 123.5 | 0 | 0
[5 empty] | 132kV |  | 123.5 | 120 | 3.5 | 3 | 2
259 |  | 132/33 KV SS Kandi | 3x50 | 150 | 132kV | 142.5 | 71.25 | 15 | 56.25 | 0 | 0
[5 empty] | 33kV |  | 71.25 | 0 | 71.25 | 0 | 4
260 |  | 132/33 KV SS Sadasivpet | 2x31.5+1x50 | 113 | 132kV | 107.35 | 53.675 | 24 | 29.675 | 0 | 0
[5 empty] | 33kV |  | 53.68 | 3 | 50.68 | 1 | 0
261 |  | 132/33 KV SS Zaheerabad | 1x80+1x50+1x31.5 | 161.5 | 132kV | 153.425 | 76.7125 | 87.3 | -10.5875 | 0 | 1
[5 empty] | 33kV |  | 76.71 | 0 | 76.71 | 0 | 2
262 |  | 132/33 KV SS Jogipet | 2x50 | 100 | 132kV | 95 | 47.5 | 0 | 47.5 | 0 | 0
[5 empty] | 33kV |  | 47.5 | 4 | 43.5 | 0 | 0
263 |  | 132/33 KV SS Pashamailaram | 4x50 | 200 | 132kV | 190 | 95 | 0 | 95 | 2 | 0
[5 empty] | 33kV |  | 95 | 0 | 95 | 0 | 2
264 |  | 132/33 KV SS Bollaram | 1x80+2x50+2x31.5 | 243 | 132kV | 230.85 | 115.425 | 0 | 115.425 | 0 | 0
[5 empty] | 33kV |  | 115.43 | 0 | 115.43 | 0 | 0
265 |  | 132/33 KV SS Narayankhed | 2x50 | 100 | 132kV | 95 | 47.5 | 0 | 47.5 | 0 | 1
[5 empty] | 33kV |  | 47.5 | 14 | 33.5 | 1 | 3
266 |  | 132/33 KV SS Gummadidala | 1x80+1x50 | 130 | 132kV | 123.5 | 61.75 | 0 | 61.75 | 1 | 2
[5 empty] | 33kV |  | 61.75 | 15 | 46.75 | 1 | 2
267 |  | 132/33 KV SS Singoor | 2x31.5 | 63 | 132kV | 59.85 | 29.925 | 0 | 29.925 | 0 | 2
[5 empty] | 33kV |  | 29.93 | 0 | 29.93 | 0 | 3
268 |  | 132/33 KV SS Patancheru | 2x50 | 100 | 132kV | 95 | 47.5 | 0 | 47.5 | 0 | 0
[5 empty] | 33kV |  | 47.5 | 0 | 47.5 | 0 | 0
269 |  | 132/33 KV SS Wattipally | 2x16 | 32 | 132kV | 30.4 | 15.2 | 0 | 15.2 | 0 | 1
[5 empty] | 33kV |  | 15.2 | 0 | 15.2 | 2 | 2
270 |  | 400/220/132 KV SS Gajwel | 2x500+2x315 | 1630 | 400kV | 1548.5 | 774.25 | 0 | 774.25 | 0 | 0
[5 empty] | 220kV |  | 774.25 | 0 | 774.25 | 0 | 0
|  |  | 3x160 | 480 | 132kV | 456 | 228 | 0 | 228 | 0 | 0
271 |  | 220/132 KV SS Siddipet | 2x100+1x160 | 360 | 220kV | 342 | 171 | 0 | 171 | 0 | 0
[5 empty] | 132kV |  | 171 | 90 | 81 | 0 | 0
272 |  | 132/33 KV SS Siddipet | 2x50+1x16 | 116 | 132kV | 110.2 | 55.1 | 0 | 55.1 |  | 0
[5 empty] | 33kV |  | 55.1 | 0 | 55.1 | 2 | 1
273 |  | 132/33 KV SS Tukkapur | 1x50+1x31.5 | 81.5 | 132kV | 77.425 | 38.7125 | 0 | 38.7125 | 0 | 0
[5 empty] | 33kV |  | 38.71 | 15 | 23.71 | 0 | 2
274 |  | 132/33 KV SS Gajwel | 2x80 | 160 | 132kV | 152 | 76 | 0 | 76 | 0 | 0
[5 empty] | 33kV |  | 76 | 0 | 76 | 1 | 0
275 |  | 132/33 KV SS Habsipur | 2x50 | 100 | 132kV | 95 | 47.5 | 0 | 47.5 | 0 | 0
[5 empty] | 33kV |  | 47.5 | 9 | 38.5 | 0 | 2
276 |  | 132/33 KV SS Thunikibollaram | 2x31.5 | 63 | 132kV | 59.85 | 29.925 | 0 | 29.925 | 0 | 0
[5 empty] | 33kV |  | 29.93 | 15 | 14.93 | 0 | 3
277 |  | 220/132/33 KV SS Meenajipet SS | 1x100 | 100 | 220kV | 95 | 47.5 | 0 | 47.5 | 0 | 2
[5 empty] | 132kV |  | 47.5 | 0 | 47.5 | 0 | 1
|  |  | 2x31.5 | 63 | 33kV | 59.85 | 29.925 | 0 | 29.925 | 0 | 3
278 |  | 132/33 KV SS Chinnashankarampet | 1x50+1x31.5 | 81.5 | 132kV | 77.425 | 38.7125 | 0 | 38.7125 | 0 | 2
[5 empty] | 33kV |  | 38.71 | 0 | 38.71 | 2 | 2
279 |  | 132/33 KV SS Palamakula | 1x50+1x31.5 | 81.5 | 132kV | 77.425 | 38.7125 | 0 | 38.7125 | 0 | 2
[5 empty] | 33kV |  | 38.71 | 15 | 23.71 | 0 | 2
280 |  | 132/33 KV SS Ganeshpally (Aungadikistapur) | 2x31.5 | 63 | 132kV | 59.85 | 29.925 | 0 | 29.925 | 0 | 2
[5 empty] | 33kV |  | 29.93 | 0 | 29.93 | 0 | 2
281 |  | 132/33 KV SS Duddeda | 2x31.5 | 63 | 132kV | 59.85 | 29.925 | 0 | 29.925 | 0 | 2
[5 empty] | 33kV |  | 29.93 | 0 | 29.93 | 0 | 2
282 |  | 132/33 KV SS Chandulapur | 2x31.5 | 63 | 132kV | 59.85 | 29.925 | 0 | 29.925 | 0 | 1
[5 empty] | 33kV |  | 29.93 | 0 | 29.93 | 0 | 2
283 |  | 132/33 KV SS Borapatla | 2x16+1x31.5 | 63.5 | 132kV | 60.325 | 30.1625 | 0 | 30.1625 | 0 | 0
[5 empty] | 33kV |  | 30.16 | 0 | 30.16 | 1 | 3
284 |  | 132/33 KV SS Doulthabad | 2x31.5 | 63 | 132kV | 59.85 | 29.925 | 0 | 29.925 | 0 | 2
[5 empty] | 33kV |  | 22.56 | 0 | 22.56 | 0 | 2
285 | Warangal | 400KV SS Jangaon | 3x500 =1500 | 1500 | 400KV | 1425 | 712.5 | 0 | 712.5 | 0 | 3
[5 empty] | 220KV |  | 712.5 | 0 | 712.5 | 0 | 4
286 |  | 220/132/33KV SS Jangaon | 2x100+1x160=360 + 2x50=100 | 360 | 220KV | 342 | 171 | 0 | 171 | 0 | 0
[5 empty] | 132KV |  | 171 | 0 | 171 | 0 | 2
|  |  |  | 100 | 33KV | 95 | 47.5 | 15 | 32.5 | 0 | 2
287 |  | 220/132/33KV SS Warangal | 3x160=480 + 2x80=160 | 480 | 220KV | 456 | 228 | 0 | 228 | 0 | 0
[5 empty] | 132KV |  | 228 | 0 | 228 | 0 | 0
|  |  |  | 160 | 33KV | 152 | 76 | 0 | 76 | 0 | 0
288 |  | 220/132/33KV SS Waddekothapally | 3x160=480 + 2x50+1x31.5=81.5 | 480 | 220KV | 456 | 228 | 0 | 228 | 0 | 0
[5 empty] | 132KV |  | 228 | 87 | 141 | 0 | 0
|  |  |  | 81.5 | 33KV | 77.425 | 38.7125 | 10 | 28.7125 | 0 | 0
289 |  | 220/132/33KV SS Mahabubabad | 2x100=200 + 1x31.5+1x16=47.5 | 200 | 220KV | 190 | 95 | 0 | 95 | 0 | 2
[5 empty] | 132KV |  | 95 | 0 | 95 | 0 | 1
|  |  |  | 47.5 | 33KV | 45.125 | 22.5625 | 0 | 22.5625 | 2 | 2
290 |  | 220/33KV SS Nagaram | 1x31.5-31.5 |  | 220KV |  | 14.9625 | 0 | 14.9625 | 0 | 2
|  |  |  | 31.5 | 33KV | 29.925 | 14.9625 | 0 | 14.9625 | 2 | 0
291 |  | 220/132/33KV SS Ammavaripet | 1x100=100 +2x50=100 | 100 | 220KV | 95 | 47.5 | 0 | 47.5 | 2 | 0
[5 empty] | 132KV |  | 47.5 | 0 | 47.5 | 2 | 2
|  |  |  | 100 | 33KV | 95 | 47.5 | 0 | 47.5 | 2 | 0
292 |  | 132/33KV SS Geesukonda | 3x31.5=94.5 | 94.5 | 132KV | 89.775 | 44.8875 | 0 | 44.8875 | 0 | 0
[5 empty] | 33KV |  | 44.8875 | 0 | 44.8875 | 0 | 2
293 |  | 132/33KV SS Nekkonda | 2x50=100 | 100 | 132KV | 95 | 47.5 | 0 | 47.5 | 0 | 2
[5 empty] | 33KV |  | 47.5 | 0 | 47.5 | 0 | 0
294 |  | 132/33KV SS Wardhannapet | 3x50=150 | 150 | 132KV | 142.5 | 71.25 | 0 | 71.25 | 0 | 2
[5 empty] | 33KV |  | 71.25 | 0 | 71.25 | 1 | 2
295 |  | 132/33KV SS Inavole | 2x31.5=63 | 63 | 132KV | 59.85 | 29.925 | 0 | 29.925 | 0 | 2
[5 empty] | 33KV |  | 29.925 | 0 | 29.925 | 2 | 2
296 |  | 132/33KV SS Narsampet | 3x31.5=94.5 | 94.5 | 132KV | 89.775 | 44.8875 | 0 | 44.8875 | 0 | 0
[5 empty] | 33KV |  | 44.8875 | 0 | 44.8875 | 0 | 2
297 |  | 132/33KV SS Gudur | 1x31.5 +1x16=47.5 | 47.5 | 132KV | 45.125 | 22.5625 | 0 | 22.5625 | 0 | 1
[5 empty] | 33KV |  | 22.5625 | 0 | 22.5625 | 0 | 2
298 |  | 132/33KV SS Peddanagaram | 1x50+1x31.5 =81.5 | 81.5 | 132KV | 77.425 | 38.7125 | 0 | 38.7125 | 0 | 1
[5 empty] | 33KV |  | 38.7125 | 0 | 38.7125 | 2 | 0
299 |  | 132/33KV SS Dornakal | 2x16 = 32 | 32 | 132KV | 30.4 | 15.2 | 0 | 15.2 | 0 | 2
[5 empty] | 33KV |  | 15.2 | 0 | 15.2 | 3 | 2
300 |  | 132/33KV SS Ayyagaripally | 2x50=100 | 100 | 132KV | 95 | 47.5 | 0 | 47.5 | 0 | 3
[5 empty] | 33KV |  | 47.5 | 0 | 47.5 | 0 | 0
301 |  | 132/33KV SS Nellikuduru | 1x50+1x31.5=81.5 | 81.5 | 132KV | 77.425 | 38.7125 | 0 | 38.7125 | 0 | 3
[5 empty] | 33KV |  | 38.7125 | 0 | 38.7125 | 2 | 2
302 |  | 132/33KV SS Ghanpur | 2x50=100 | 100 | 132KV | 95 | 47.5 | 0 | 47.5 | 0 | 0
[5 empty] | 33KV |  | 47.5 | 0 | 47.5 | 0 | 1
303 |  | 132/33KV SS Palakurthy | 2x50=100 | 100 | 132KV | 95 | 47.5 | 0 | 47.5 | 0 | 4
[5 empty] | 33KV |  | 47.5 | 0 | 47.5 | 0 | 2
304 |  | 132/33KV SS Raghunathpally | 2x50=100 | 100 | 132KV | 95 | 47.5 | 0 | 47.5 | 0 | 0
[5 empty] | 33KV |  | 47.5 | 0 | 47.5 | 0 | 3
305 |  | 132/33KV SS Narmetta | 2x31.5=63 | 63 | 132KV | 59.85 | 29.925 | 0 | 29.925 | 0 | 2
[5 empty] | 33KV |  | 29.925 | 0 | 29.925 | 0 | 2
306 |  | 132/33KV SS Mustyal | 2x50+1x31.5=131.5 | 131.5 | 132KV | 124.925 | 62.4625 | 0 | 62.4625 | 0 | 2
[5 empty] | 33KV |  | 62.4625 | 10 | 52.4625 | 0 | 0
307 |  | 132/33KV SS Bachannapet | 3x16=48 | 48 | 132KV | 45.6 | 22.8 | 0 | 22.8 | 0 | 3
[5 empty] | 33KV |  | 22.8 | 0 | 22.8 | 2 | 2
308 |  | 132/33KV SS Pasra | 2x16=32 | 32 | 132KV | 30.4 | 15.2 | 0 | 15.2 | 0 | 2
[5 empty] | 33KV |  | 15.2 | 0 | 15.2 | 0 | 3
309 |  | 132/33KV SS Chityala | 2x50=100 | 100 | 132KV | 95 | 47.5 | 0 | 47.5 | 0 | 1
[5 empty] | 33KV |  | 47.5 | 0 | 47.5 | 2 | 2
310 |  | 132/33KV SS Kamalapur | 2x31.5=63 | 63 | 132KV | 59.85 | 29.925 | 0 | 29.925 | 0 | 2
[5 empty] | 33KV |  | 29.925 | 0 | 29.925 | 0 | 2
311 |  | 132/33KV SS Mulugu | 3x31.5 =94.5 | 94.5 | 132KV | 89.775 | 44.8875 | 0 | 44.8875 | 0 | 0
[5 empty] | 33KV |  | 44.8875 | 0 | 44.8875 | 0 | 0
312 |  | 132/33KV SS Chelpur | 1x50+1x31.5=81.5 | 81.5 | 132KV | 77.425 | 38.7125 | 0 | 38.7125 | 0 | 2
[5 empty] | 33KV |  | 38.7125 | 10 | 28.7125 | 0 | 1
313 |  | 132/33KV SS Waddepally | 3x50=150 | 150 | 132KV | 142.5 | 71.25 | 0 | 71.25 | 0 | 0
[5 empty] | 33KV |  | 71.25 | 0 | 71.25 | 1 | 3
314 |  | 132/33KV SS Regonda | 3x16=48 | 48 | 132KV | 45.6 | 22.8 | 0 | 22.8 | 0 | 1
[5 empty] | 33KV |  | 22.8 | 0 | 22.8 | 1 | 2
[7 empty] | 64220.9625 | 3753.8 | 60467.1625

## Abstract
Abstract
Circle wise Total Injection,existing and balance available capacities for RE injection
Sl.No | Name of the SE/OMC Circle | Total Injection Capacity of all the buses | Existing RE Injection Capacity | Balance Capacity available for Injection
1 | Adilabad | 2566.2 | 349 | 2217.2
2 | Karimnagar | 4476.9075 | 244 | 4232.9075
3 | Khammam | 3685.52 | 176 | 3509.52
4 | Mahabubnagar | 6592.6725 | 1029.2 | 5563.4725
5 | Metro-Central | 4265.5 | 0 | 4265.5
6 | Metro-East | 9292.905 | 32 | 9260.905
7 | Metro-West | 7536.8425 | 213.8 | 7323.0425
8 | Nalgonda | 8555.95 | 448.5 | 8107.45
9 | Nizamabad | 4605.125 | 423 | 4182.125
10 | Sangareddy | 7474.145 | 706.3 | 6767.845
11 | Warangal | 5084.4 | 132 | 4952.4
| Total | 64136.1675 | 3753.8 | 60382.3675
Note on A3: Author:

## Voltage Vs Capacity
Voltage wise allowable RE injection Capacities
Sl.No | Injecting sub-station | Injection voltage level | Injection capacity at Sub-station
1 | 33/11 | 11 kV | Up to 3 MW
2 | 33/11 | 33 kV | 3.001 to 10 MW
3 | 132/33 | 33 kV | 10.001 to 20 MW
4 | 132/33 | 132 kV | 20.001 to 50 MW
5 | 220/132 | 132 kV | 20.001 to 80 MW
6 | 220/132 | 220 kV | 80.001 to 100 MW
7 | 400/220 | 220 kV | 80.001 to 150 MW
8 | 400/220 | 400 kV | Above 150 MW