ORDER NO:137 DT: 05.12.2013

- TRANSMISSION CORPORATION OF ANDHRA PRADESH LIMITED

O/o SUPERINTENDING ENGINEER,

TL&SS CIRCLE ::  KADAPA.

Memo.No.SE/TL & SS/Kdp/ADET/AET /F.40 ./D.No.                 /13, Dt.     -11-13.

Sub:  APTRANSCO  - TL&SS Circle /Kadapa –  “Fixing of vibration dampers

suitable  for DEER ACSR conductor in 220 KV Kadapa – Mydukur (SC) line

from Loc.No. 1 to 103 at all suspension points in EHT lines Sub-Division

Kadapa – Estimate – Sanctioned – Reg.

Ref:  Lr.No.DE/TL & SS/Kdp/F.26/D.No.1745/13,Dt. 04-11-13.

- - -

Under the  powers delegated vide T.O.O.No.CE(Transmission) MS.No.229,

Dt. 18-09-10, item  No.4(b) of revised delegation of powers, the under signed is pleased to accord sanction to the estimate towards “Fixing of vibration dampers suitable  for DEER ACSR conductor in 220 KV Kadapa – Mydukur (SC) line from Loc.No. 1 to 103 at all suspension points in EHT lines Sub-Division/Kadapa”.

The cost of the estimate works out to Rs. 95,257.00  (Rupees Ninety five  thousand two hundred and fifty seven only)

The estimate  is technically sanctioned and registered as O&M  No.56 /13-14  and the work should be taken up subject availability budget provision.

The expenditure is chargeable to A/C.No. 74.500 of 220 KV SS/ Kadapa under TL & SS  Division, Kadapa   under O&M of lines cables, net work etc.,

Encl: 1 No. Estimate.				SUPERINTENDING ENGINEER,

TL & SS CIRCLE :: KADAPA.

To

The Divisional Engineer/TL & SS/Kadapa.

The Asst. Divisional Engineer/M/220KV SS/Mydukur.

# Along with estimate  Encl: One estimate

Copy submitted to the Chief Engineer/Kadapa Zone/Kadapa.

Copy to the Accounts Officer/TL & SS Circle/Kadapa.

REPORT TO ACCOMPANY THE ESTIMATE

NAME OF THE WORK:   “Fixing of vibration dampers suitable for DEER ACSR conductor in 220 KV Kadapa – Mydukur (SC) line from Loc.No. 1 to 103 at all suspension points in EHT lines Sub-Division/Kadapa.

PROPOSAL IN BRIEF:  The proposals of estimate envisages for Fixing of vibration dampers suitable for DEER ACSR conductor in 220 KV Kadapa – Mydukur (SC) line from Loc.No. 1 to 103 at all suspension points in EHT lines Sub-Division/Kadapa.  The 220 KV Kadapa – Mydukur (SC) line was commissioned long back during the year 1969 and the tower locations (suspension points) are not provided with vibration dampers.  It is essential to provide vibration dampers at all suspension points in order to minimize vibrations of power conductor. Further, the quality assurance also instructed to provide vibration dampers at all locations to provide reliable supply.  Hence the estimate is prepared for labour portion for fixing of vibration dampers in 220 KV Kadapa – Mydukur (SC) line at all suspension points.

COST OF THE ESTIMATE:  The estimate is prepared based on SSR of APTRANSCO for the year 2013-14 and worked out to Rs. 95,257.00 (Rupees Ninety five thousand two hundred and fifty seven only) and the expenditure may be chargeable to A/C.No. 74.500 towards O&M of EHT lines, cables, network etc., of EHT lines Sub-Division, Kadapa  for the year 2013-14.

CONCLUSION:  The estimate is now sanctioned.

ABSTRACT ESTIMATE

| S.No. | Description | Qty | Rate/Per | Amounrt |
| --- | --- | --- | --- | --- |
| 1 | Fixing of vibration dampers for DEER ACSR conductor in 220 KV Kadapa – Mydukur line (As per Data) | 516 Nos. | 164.30/Each | 84,778.80 |
|  | Add Service Tax @ 12.36% on item (1) |  |  | 10478.66 |
|  | TOTAL |  |  | 95257.00 |

Or say  Rs. 95,257.00 (Rupees Ninety five thousand two hundred and fifty seven only)

MATERIAL/EQUIPMENT RATES

| S.No. | Description of work | Amount |
| --- | --- | --- |
| 1. | Fixing of vibration dampers for DEER ACSR conductor in 220 KV Kadapa – Mydukur line (As per Data) page No. 290 of APTRANSCO SSR 13-14 | 106.00 |
| 2. | Add mobilization charges @ 5% on item (1) as per SSR | 5.30 |
| 3. | Add 50% extra on item (1) towards shutdown charges | 53.00 |
|  | Total | 164.30 |

SUPERINTENDING ENGINEER,

TL & SS CIRCLE :: KADAPA

DATA – I

Details of locations not having Vibration dampers in 220KV Kadapa – Mydukur (SC) line

| Tower Loc. No. | Type of tower | Qty required | Tower Loc. No. | Type of tower | Qty required |
| --- | --- | --- | --- | --- | --- |
| 1. | Z | - | 54 | A1 | 6 |
| 2 | X | 6 | 55 | A1 | 6 |
| 3 | X | 6 | 56 | A1+3 | 6 |
| 4 | Z | - | 57 | A1 | 6 |
| 5 | B1 | - | 58 | A1 | 6 |
| 6 | Bt | - | 59 | A1 | 6 |
| 7 | Bt | - | 60 | A1 | 6 |
| 8 | B1 | - | 61 | A1 | 6 |
| 9 | A1 | 6 | 62 | A1 | 6 |
| 10 | A1 | 6 | 63 | A1 | 6 |
| 11 | A1 | 6 | 64 | A1 | 6 |
| 12 | A1 | 6 | 65 | A1 | 6 |
| 13 | B | - | 66 | A1 | 6 |
| 14 | A1 | 6 | 67 | B1 | - |
| 15 | A1 | 6 | 68 | A1 | 6 |
| 16 | C1 | - | 69 | A1 | 6 |
| 17 | A1 | 6 | 70 | A1 | 6 |
| 18 | A1 | 6 | 71 | A1 | 6 |
| 19 | A1 | 6 | 72 | A1 | 6 |
| 20 | A1 | 6 | 73 | A1 | 6 |
| 21 | A1 | 6 | 74 | A1 | 6 |
| 22 | B1 | - | 75 | A1 | 6 |
| 23 | A1 | 6 | 76 | A1 | 6 |
| 24 | A1 | 6 | 77 | A1 | 6 |
| 25 | A1 | 6 | 78 | A1 | 6 |
| 26 | A1+3 | 6 | 79 | A1 | 6 |
| 27 | A1+3 | 6 | 80 | A1 | 6 |
| 28 | A1 | 6 | 81 | A1 | 6 |
| 29 | A1 | 6 | 82 | B1 | - |
| 30 | A1 | 6 | 83 | A1 | 6 |
| 31 | A1 | 6 | 84 | A1 | 6 |
| 32 | A1 | 6 | 85 | A1 | 6 |
| 33 | A1 | 6 | 86 | A1 | 6 |
| 34 | A1 | 6 | 87 | A1 | 6 |
| 35 | B1 | - | 88 | A1 | 6 |
| 36 | A1 | 6 | 89 | A1 | 6 |
| 37 | A1 | 6 | 90 | A1 | 6 |
| 38 | A1 | 6 | 91 | A1 | 6 |
| 39 | A1 | 6 | 92 | A1 | 6 |
| 40 | A1 | - | 93 | A1 | 6 |
| 41 | A1 | 6 | 94 | B1 | - |
| 42 | A1 | 6 | 95 | A1 | 6 |
| 43 | A1 | 6 | 96 | A1 | 6 |
| 44 | A1 | 6 | 97 | A1 | 6 |
| 45 | A1 | 6 | 98 | A1+3 | 6 |
| 46 | A1+3 | 6 | 99 | A1 | 6 |
| 47 | A1 | 6 | 100 | A1 | 6 |
| 48 | Bt | - | 101 | A1+3 | 6 |
| 49 | A1 | 6 | 102 | A1 | 6 |
| 50 | A1+3 | 6 | 103 | B1 | - |
| 51 | C1+3 | - | 103/1 | C | - |
| 52 | C1+3 | - | 103/2 | A | 6 |
| 53 | C1 | - | 103/3 | A | 6 |
|  |  |  | 103/4 | C | - |
|  |  |  |  | Total Qty | 516 Nos |

SUPERINTENDING ENGINEER,

TL & SS CIRCLE :: KADAPA