- ORDER NO:139 DT: 05.12.2013

- TRANSMISSION CORPORATION OF ANDHRA PRADESH LIMITED

O/o SUPERINTENDING ENGINEER,

TL&SS CIRCLE ::  KADAPA.

Memo.No.SE/TL & SS/Kdp/ADET/AET /F.40 ./D.No.                 /13, Dt.     -11-13.

Sub:  APTRANSCO  - TL&SS Circle /Kadapa – Replacement of defective 33 KV

Rallabuduguru feeder breaker (Make:ABB, SF6, S.No.IB235600) at 132 KV

SS Santhipuram – Estimate – Sanctioned – Reg.

Ref:   Lr.No.DE/TL & SS/CTR/Tech/MF.No.04/D.No.1034/13,Dt. 12-11-13.

- - -

Under the powers delegated vide T.O.O.No.CE (Transmission)Ms.No.

229, Dt.18-9-10 item No. 4(b) enhancement of delegation of powers, the undersigned is pleased to accord sanction to the estimate for ”Replacement of defective 33 KV Rallabuduguru feeder breaker (Make:  ABB, SF6, S.No.IB235600) at 132 KV SS Santhipuram

The cost of the estimate works out to Rs. 1,77,704.00 (Rupees One lakh Seventy seven thousand seven hundred and four only)

The estimate  is technically sanctioned and registered as RMI No.58/13-14  and the work should be taken up subject availability budget provision.

The expenditure is chargeable to A/C.No. 14.500 of 132 KV SS Santhipuram under TL & SS  Division, Chittoor   under RMI for the year 2013-14.

Encl: 1 No. Estimate.				SUPERINTENDING ENGINEER,

TL & SS CIRCLE :: KADAPA.

To

The Divisional Engineer/TL & SS/Chittoor.

The  ADE/M/220 KV SS/Palamaner.

# Along with estimate  Encl: One estimate

Copy to the Executive Engineer/Civil/TLC/Kadapa.

Copy to the Asst. Executive Engineer/O&M/Civil/Tirupati.

Copy submitted to the Chief Engineer/Kadapa Zone/Kadapa.

Copy to the Accounts Officer/TL & SS Circle/Kadapa.

REPORT TO ACCOMPANY THE ESTIMATE

NAME OF THE WORK:   The estimate envisages for replacement of defective 33 KV Rallabuduguru Feeder Breaker (Make: ABB, SF6,S.No.IB 235600) at 132 KV SS Santhipuram.

PROPOSAL IN BRIEF:    The estimate envisages for replacement of defective 33 KV Rallabuduguru Feeder Breaker (Make: ABB, SF6,S.No.IB 235600) at  132 KV SS Santhipuram.  The breaker essentially needs replacement, i.e., served more than 20 years (year of manufacturing-1991) D.O.C. 20-02-1993.  At present the Breaker is giving frequent  mechanical troubles i.e. spring charge mechanism problem and also the SF6 gas leakage is observed through “O” rings at many places and hence frequent SF6 gas filling is necessary which is time consuming process and also if any limb fails, no spares available to meets emergency, during the inspection of higher officials to 132 KV SS Santhipuram it is suggests for replacement of above said breaker is essential with new one.

COST OF THE ESTIMATE:  The cost of the estimate works out to Rs. 1,77,704.00 (Rupees One lakh Seventy seven thousand seven hundred and four only) and the expenditure is chargeable to RMI works of 132 KV SS, Santhipuram for the year 2013-14.

CONCLUSION :  The  estimate is now sanctioned.

SUPERINTENDING ENGINEER,

TL & SS CIRCLE :: KADAPA

DETAILED ESTIMATE

NAME OF THE WORK:   The estimate envisages for replacement of defective 33 KV Rallabuduguru Feeder  breaker (Make: ABB, SF6,S.No.IB 235600) at 132 KV SS Santhipuram

| S. No. | Description | Qty |  | Rate/Per | Material | Labour Amount |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | RCC m20 nominal mix(cement5 350 Kgs) using 20mm size graded machine crushed granite metal including cost and conveyance of all materials like cement, sand, water etc to site and includes seigniorage charges all taxes on materials, labour charges, machine mixing, laying concrete, vibrating, centering curing etc complete(but excluding cost of steel and its fabrication) for finished item of work as directed by the engineer in charge | 1.0 | Cum | 6530,14 |  | 6530.14 |
| 2 | Supplying, fitting and placing HYSD/TMT bar reinforcement in foundation of plinth as per specifications for bars below 36mm dia includes over laps and wastage, including cutting, bending,cranking, typing in position including cost of banding wire etc complete for finished item of work | 30 | Kg | 55.55 |  | 1666.50 |
| 3. | Loading/un loading of 33 KV breaker at stores and at site respectively page no. 18 item No. S.No.ST35 as per SSR | 2 | Nos. | 852.10 |  | 1704.20 |
| 4 | Handling charges for the erection of the 33 KV Breaker by utilising the 2T crane as per SSR 12-13 rates in place of defective ABB Make SF6 breaker Page:,20,ST90,Item No.53 SSR 2013-14 | 1st Additional | Hr. Hr. | 2082.50 945.90 |  | 3028.40 |
| 5 | Providing of earth mate to structures by cutting , bending and welding to the structures and existing earth mat 50 X 8mm Page:13 CS 17 of SSR 13-14 | 10 | Mtr | 58.20 |  | 582.00 |
| 6 | Cost of the high speed blades for cutting the jumper for providing jumpers to new breaker and old CT’s | 4 | Nos. | 50.00 |  | 200.00 |
| 7 | Providing of various holes for cable entry to the base plate of breaker mechanism | 5 | Nos. | 20.00 |  | 100.00 |
| 8 | Cost of 33 KV Breaker (VCB) | 1 | No. |  | 163210.00 | 13811.24 |
|  | Service Tax @ 12,36% on 40% on Sub-Total excluding item No. (8) |  |  |  |  | 682.82 |
|  | Total Rs. |  |  |  |  | 177704.06 |
|  | Or say Rs. |  |  |  |  | 177704.00 |

Rs. 1,77,704.00 (Rupees One lakh Seventy seven thousand seven hundred and four only)

SUPERINTENDING ENGINEER,

TL & SS CIRCLE :: KADAPA