ORDER NO: 145, DT: 05.12.2013

- TRANSMISSION CORPORATION OF ANDHRA PRADESH LIMITED

O/o SUPERINTENDING ENGINEER,

TL&SS CIRCLE ::  KADAPA.

Memo.No.SE/TL & SS/Kdp/ADET/AET /F.40 ./D.No.                 /13, Dt.     -11-13.

Sub:  APTRANSCO  - TL&SS Circle /Kadapa –  Replacement of 1 No. new battery

set of 220 V, 80AH along with battery charger at 132 KV SS, Burakayala Kota

– Estimate – Sanctioned – Reg.

Ref:    Lr.No.DE/TL & SSCTR/Tech/MF.No.04/1067/13,Dt. 20-11-13.

- - -

Under the powers delegated vide T.O.O.No.CE (Transmission) Ms.No.229,Dt.18-9-10 item No. 4(b) enhancement of delegation of powers, the undersigned is pleased to accord sanction to the estimate for Replacement of 1 No. new battery set of 220 V, 80AH along with battery charger at 132 KV SS, Burakayala Kota.

The cost of the estimate works out to Rs. 2,75,191.00 (Rupees Two lakhs seventy five thousand one hundred and ninety one  only)

The estimate  is technically sanctioned and registered as RMI No. 64 /13-14  and the work should be taken up subject availability budget provision.

The expenditure is chargeable to A/C.No. 14.500 of 132KV SS Burakayala Kota  under TL & SS  Division,Chittoor  under RMI for the year 2013-14.

Encl: 1 No. Estimate.				SUPERINTENDING ENGINEER,

TL & SS CIRCLE :: KADAPA.

To

The Divisional Engineer/TL & SS/Chittoor.

The  ADE/M/220 KV SS/Kalikiri.

# Along with estimate  Encl: One estimate

Copy submitted to the Chief Engineer/Kadapa Zone/Kadapa.

Copy to the Accounts Officer/TL & SS Circle/Kadapa.

REPORT TO ACCOMPANY THE ESTIMATE

NAME OF THE WORK: The estimate envisages for providing of new 80AH lead acid battery bank and charger, at 132 KV SS, Burakayala Kota.

PROPOSAL IN BRIEF:  The estimate envisages for providing of  new 80AH Lead acid battery set and charger as the performance of the existing battery bank is poor.  The exising batteries had served for 14 years.  The electrolyte level falls down every week even after adding of distilled water and specific gravities of battery cells are increasing to high levels. The battery charger is having frequent problems and causing emergencies.  The Float charger turns off automatically  at certain instances.  It is essential to replace the existing battery bank and charger to avoid emergencies.  The details of the battery bank and charger  to avoid emergencies. The details of the battery  bank and charger are herewith furnished.

Batteries			Charger

Make	:  				STANDARD			HEE

Capacity:				80AH				16 A

Year of Mfg.				--				1997

D.O.C					27-03-1999			27-03-1999

Hence the proposal submitted for new battery bank and charger.

COST OF THE ESTIMATE:  The estimate is prepared based on SSR of APTRANSCO for the year 2013-14 and worked out to Rs. 2,75,191.00 (Rupees Two lakhs seventy five thousand one hundred and ninety one  only) and is  chargeable to R&M works of 132KV SS Burakayala Kota   for the year 2013-14.

CONCLUSION:  The estimate is now sanctioned.

DETAILED ESTIMATE

| S.No. | Particulars | Qty | Rate | Material | Labour |
| --- | --- | --- | --- | --- | --- |
| 1 | Loading charges for loading of 220V 80AH battery set (Lead acid) at stores as per SSR 2013-14 | 1 set | 709.20 |  | 709.20 |
| 2 | Unloading charges for un loading of 80AH battery set at 132 KV SS Burakayala Kota as per SSR 2013-14 | 1 Set | 709.20 |  | 709.20 |
| 3 | Loading charges for loading of 220 V battery charger with DCDB at Stores, as per SSR 2013-14 | 1 Set | 426.10 |  | 426.10 |
| 4 | Unloading charges for unloading of 220 V, 80AH Battery charger at 132 KV SS Burakayalakota as per SSR 2013-14 | 1 Set | 426.10 |  | 426.10 |
| 5 | Erection of new 220 V, 200Ah/80Ah battery set in complete shape fit for charging (Lead acid) as per ERP | 1 Set |  | 186236.00 | 8315.00 |
| 6 | Erection of new 220 V, 200Ah/80Ah battery charges with DC/DB as per ERP | 1 Set |  | 73956.00 | 2763.00 |
|  | Sub-total Rs. |  |  | 260192.00 | 13348.60 |
|  | Service charges 12.36% on Labour |  |  |  | 1649.88 |
|  | Grand Total (Material + Labour) |  |  |  | 275190.48 |
|  | Or say Rs. |  |  |  | 275191.00 |

Rs. 275191.00 (Rupees Two lakhs seventy five thousand one hundred and ninety one  only)

SUPERINTENDING ENGINEER,

TL & SS CIRCLE :: KADAPA